## Sheet1
Equipment # | Issues | Resolution
545 BM 1 | Service request: Isolate supply | Isolate & normalize supply
545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
545 BM 1 | Service request: Isolate supply | Isolate & normalize supply
545 BM 1 | Insulation Test | Test for spare motor.
545 BM 1 | Insulation Test | Test for spare motor.
545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
545 BM 1 | Service request: Isolate supply | Isolate & normalize supply
545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
545 BM 1 | Insulation test | Test for spare motor.
545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
545 BM 1 | Insulation test | Test for spare motor.
545 BM 1 | Insulation test | Test for spare motor.
545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
545 BM 1 | Service request: Isolate supply | Isolate & normalize supply
545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
545 BM 1 | Service request: Isolate supply | Isolate & normalize supply
545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
545 FN 16 | Service request: Isolate supply | Isolate & normalize supply
545 FN 16 | Maintenance routine | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
545 FN 16 | Service request: Isolate supply | Isolate & normalize supply
545 FN 16 | Maintenance routine | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
545 FN 16 | Maintenance routine | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
545 FN 16 | Service request: Isolate supply | Isolate & normalize supply
545 FN 16 | Maintenance routine | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
545 FN 16 | Service request: Isolate supply | Isolate & normalize supply
545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
545 FN 16 | Service request: Isolate supply | Isolate & normalize supply
545 FN 16 | Maintenance routine | Motor and starter maintenance. Blow motor, slip ring and filter. Lift up resistance starter and check all contact and resistor. Dismantle all fixed and moving contact bring back to workshop. Repair and service all the contact piece. Reinstall to starter, cleaning and renew oil.
545 FN 16 | Maintenance routine | Motor and starter maintenance. Blow motor, slip ring and filter. Lift up resistance starter and check all contact and resistor. Dismantle all fixed and moving contact bring back to workshop. Repair and service all the contact piece. Reinstall to starter, cleaning and renew oil.
545 FN 16 | Maintenance routine | Motor and starter maintenance. Blow motor, slip ring and filter. Lift up resistance starter and check all contact and resistor. Dismantle all fixed and moving contact bring back to workshop. Repair and service all the contact piece. Reinstall to starter, cleaning and renew oil.
545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
545 FN 16 | Maintenance routine | Motor and starter maintenance. Blow motor, slip ring and filter. Lift up resistance starter and check all contact and resistor. Dismantle all fixed and moving contact bring back to workshop. Repair and service all the contact piece. Reinstall to starter, cleaning and renew oil.
545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
545 FN 16 | Maintenance routine | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
550 RP 1 | Service request: Isolate supply | Isolate & normalize supply
550 RP 1 | Service request: Isolate supply | Isolate & normalize supply
550 RP 1 | Service request: Isolate supply | Isolate & normalize supply
550 RP 1 | Service request: Isolate supply | Isolate & normalize supply
550 RP 1 | Service request: Isolate supply | Isolate & normalize supply
550 RP 1 | Maintenance routine | Check carbon/brush, s/ring and starter
550 RP 1 | Maintenance routine | Check carbon/brush, s/ring and starter
550 RP 1 | Maintenance routine | Check carbon/brush, s/ring and starter
550 RP 1 | Maintenance routine | Check carbon/brush, s/ring and starter
550 RP 1 | Maintenance routine | Check carbon/brush, s/ring and starter
550 RP 1 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
550 RP 1 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
550 RP 1 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
550 RP 1 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
550 RP 1 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
550 RP 1 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
550 RP 1 | Maintenance routine | Greasing motor
550 RP 1 | Maintenance routine | Greasing motor
550 RP 1 | Maintenance routine | Greasing motor
550 RP 1 | Maintenance routine | Greasing motor
550 RP 1 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
550 RP 1 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
550 RP 1 | Maintenance routine | Greasing motor
561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
561 RL 1 | Maintenance routine | HT motor monitoring. Monitor carbon brush, slip ring and starter condition for the following motor.
561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
561 RL 1 | Maintenance routine | HT motor monitoring. Monitor carbon brush, slip ring and starter condition for the following motor.
561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
561 RL 1 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition for the following motor.
561 RL 1 | Maintenance routine | HT motor monitoring. Monitor carbon brush, slip ring and starter condition for the following motor.
561 RL 1 | Maintenance routine | Top up 24 liter distill water for starter
561 RL 1 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition for the following motor.
561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
561 RL 1 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition for the following motor.
561 RL 1 | Maintenance routine | HT motor monitoring. Monitor carbon brush, slip ring and starter condition for the following motor.
561 RL 1 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition for the following motor.
561 RL 1 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition for the following motor.
561 RL 1 | Maintenance routine | Greasing motor
561 RL 1 | Maintenance routine | Greasing motor
561 RL 1 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition for the following motor.
561 RL 1 | Maintenance routine | Top up 24 liter distill water for starter
561 RL 1 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition for the following motor.
561 RL 1 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition for the following motor.
561 RL 1 | Maintenance routine | Greasing motor
561 RL 1 | Maintenance routine | Greasing motor
545 BM 1 | Insulation test | Test for spare motor.
545 BM 1 | Service request: Isolate supply | Isolate & normalize supply
545 FN 16 | Maintenance routine | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
545 FN 16 | Maintenance routine | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
545 FN 16 | Maintenance routine | Motor and starter maintenance. Blow motor, slip ring and filter. Lift up resistance starter and check all contact and resistor. Dismantle all fixed and moving contact bring back to workshop. Repair and service all the contact piece. Reinstall to starter, cleaning and renew oil.
545 FN 16 | Maintenance routine | Motor and starter maintenance. Blow motor, slip ring and filter. Lift up resistance starter and check all contact and resistor. Dismantle all fixed and moving contact bring back to workshop. Repair and service all the contact piece. Reinstall to starter, cleaning and renew oil.
545 FN 16 | Maintenance routine | Motor and starter maintenance. Blow motor, slip ring and filter. Lift up resistance starter and check all contact and resistor. Dismantle all fixed and moving contact bring back to workshop. Repair and service all the contact piece. Reinstall to starter, cleaning and renew oil.
545 FN 16 | Service request: Isolate supply | Isolate & normalize supply
545 FN 16 | Service request: Isolate supply | Isolate & normalize supply
545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
550 RP 1 | Maintenance routine | Check carbon/brush, s/ring and starter
550 RP 1 | Maintenance routine | Greasing motor
550 RP 1 | Service request: Isolate supply | Isolate & normalize supply
550 RP 1 | Service request: Isolate supply | Isolate & normalize supply
561 RL 1 | Maintenance routine | Greasing motor
561 RL 1 | Maintenance routine | Greasing motor
561 RL 1 | Maintenance routine | Top up 24 liter distill water for starter
561 RL 1 | Maintenance routine | Top up 24 liter distill water for starter
561 RL 1 | Maintenance routine | Top up 24 liter distill water for starter
561 RL 1 | Maintenance routine | Top up 24 liter distill water for starter
561 RL 1 | Maintenance routine | HT motor monitoring. Monitor carbon brush, slip ring and starter condition for the following motor.
561 RL 1 | Maintenance routine | HT motor monitoring. Monitor carbon brush, slip ring and starter condition for the following motor.
561 RL 1 | Maintenance routine | HT motor monitoring. Monitor carbon brush, slip ring and starter condition for the following motor.
561 RL 1 | Maintenance routine | HT motor monitoring. Monitor carbon brush, slip ring and starter condition for the following motor.
561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
562 MW | Overload | Isolate & normalize supply
545 FN 4 | Rack in ACB | Close ACB
545 FN 4 | Rack out ACB | Open ACB
CM3 | Trip | Isolate & normalize supply
CM3 | CM3 & CM4 running smoothly | Standby
545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
CM3 | Running smoothly | Standby
545 FN 4 | Service request: Normalize fuse form | Normalize fuse form
CM3 | cable snap | Rejoint cable and restart
545 FM 2 | AL10 alarm flow high | Isolate & normalize supply
561 CP 1 | Trip by alarm element outlet temp. | Isolate & normalize supply
555 CP 3 | Service request: Isolate supply | Open ACB
561 CP 1 | Miller req to check alarm not ready | Isolate & normalize supply
545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
561 CP 1 | Alarm almost collect | Isolate & normalize supply
561 CP 2 | Service request: Isolate supply | Isolate & normalize supply
561 CP 2 | Alarm overload at CCR | Check at CP alarm service required. Check status alarm DP oil separator service max 0.80 bar. Reset
545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
54A BM 1 | Insulation test | Inject 6kv - 0 ohm. Inject 1kv - 8 ohm
555 CP 3 | Service request: Isolate supply | Isolate & normalize supply
545 FM 2 | AL 10 flow to high | Isolate & normalize supply
545 FM 2 | AL10 flow too high | Isolate & normalize supply
555 CP 3 | Maintenance routine | Greasing the following motor
555 CP 3 | Service request: Isolate supply | Isolate & normalize supply
555 CP 3 | Service request: Isolate supply | Isolate & normalize supply
545 FM 2 | AL10 flow too high | Isolate & normalize supply
561 CP 2 | Breaker for cooling fan damage | Replace breaker
555 CP 3 | Alarm at temp | Isolate supply and normalize supply
542 BC 4 | Overload | Isolate & normalize supply
561 CP 1 | Overload | Isolate & normalize supply
561 CP 2 | Can't start from CCR | Maintenance fault. Found CP in local mode. Change to remote.
561 CP 2 | Overload fan motor | Isolate & normalize supply
555 CP 3 | Service request: Isolate supply | Isolate supply and normalize supply
555 CP 3 | Service request: Isolate supply | Isolate & normalize supply
545 FM 2 | AL10 flow to figh | Isolate & normalize supply
CM3 | Insulation test | Test for transformer. R-E: 1.4 ohm, Y-E: 1.4 ohm, B-E: 1.4 ohm
CM3 | WO: CE 879 : Miller request to check group. Group 545 and 535 trip. | Check at ER5 trip incoming. Check and found breaker for 545 FN 13 trip. Perform insulation test at terminal, result show motor short. Replace motor and test.
542 BC 4 | Monitoring | Remonitoring LV Motor for bearing replacement on CNY.
561 CP 1 | Alarm | Isolate & normalize supply
561 CP 1 | Return fault at CCR | Check at Panel CP alarm starter feedback contact. Reset. Restart still return fault. Contactor not energize. Indicator " Comp run" at controller showing run. Attendant check oil leak. Try local motor still not run. Suspect safety sensor out off or controller problem. Need to follow up - trip.
561 CP 2 | Not load | Disconnect, cut & rejoint cable.
545 FN 4 | Isolate supply | Isolate & normalize supply
561 CP 2 | Socker valve problem | Repair socker valve
561 CP 1 | open switch | By pass temp switch
54A BM 1 |  | Lay cable (fly) from MCC CM1, to main drive motor and to winding motor for heating. Motor already baricate. Amp - R-3.2A. Y-3.2A, B-3.2A.
54A BM 1 | Troubleshoot | Disconnect cable supply for heating and bring to work shop
555 CP 3 | Isolate supply | Open ACB. Rack out.
542 BC 4 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
542 BC 4 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
542 BC 4 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6307
542 BC 4 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6206
561 CP 2 | Alarm overload at CCR | Check at CP alarm. Service DP air filter
542 BC 4 | Isolate supply | Off MCCB
555 CP 3 | Isolate supply | Off MCCB
542 BC 4 | Maintenance routine (CNY 2024 stoppage) | ContInue service motor WO : EE 770/ oil seal
542 BC 4 | Installation | Install and dismantle motor CM3 - Ready to install. After completing the service do an insulation test
542 BC 4 | Installation | Install motor CM5
54A BM 1 | Power cut | Power cut Cement Mill & Packing plant
542 BC 4 | Installation | Install motor at site
CM3 | Hoist not function | Check found supply. Genset not running. Genset problem 2x stop. Follow up needed.
555 CP 3 | Normalize fuse form | On MCCB
CM3 | Siren Mill. Siren roller press | Replace new siren. Siren roller press test.
CM3 | Service request: Isolate supply | Isolate & normalize supply
CM3 | Lay cable for main drive CM3 - damaged | Prepare for cable pointer. Follow up needed.
545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
542 BC 4 | Overload 4x | Isolate & normalize supply
545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
542 BC 4 | Overload 4x | Isolate & normalize supply
545 FN 4 | maintenance routine | Greasing motor
545 FN 4 | Service request: Isolate supply | Rack ACB & close
542 BC 4 | Overload | Isolate & normalize supply
555 CP 3 | maintenance routine | Greasing the following motor
561 CP 1 | maintenance routine | Greasing the following motor
561 CP 2 | maintenance routine | Greasing the following motor
54A BM 1 | Starter problem | Check condition starter. Test manual ok. Lift up rheostart & check condition. Follow up needed.
561 CP 1 | Compressor breakdown | Find cable for rental compressor 120mm3. Follow up needed.
561 CP 2 | Service request: Isolate supply | Isolate & normalize supply
561 CP 2 | Cable not available | Lay temporary cable for rental compressor. 1 core 95 mm3 aluminium x 7 x 30 m connect at MCC and compressor. Follow up for testing.
561 CP 2 | Compressor testing | Rental compressor. Commissioning rental compressor. Unload - 150 A (R,Y,B). Load 230 A (R,Y,B)
561 CP 2 | Compressor installation | CNB 3:9:3.
54A BM 1 | Troubleshoot | Starter. Connect back control cable and rotor cable. Check star point contactor. Ready for testing
CM3 | Replace 1 pc LED sportlight. 100 watt | Replace 1 pc LED sportlight. 100 watt
54A BM 1 | Test switchgear spring tension snap during test | Check and repeat another one testing. Send to PL1 reading for starter testing.
545 FN 4 | Alarm vibration 545 FN4 VD1. V41 | Reset failed. Follow up needed.
54A BM 1 | Motor Testing | Test control motor. Starter up and down position ok. Start point contactor ok. Switch gear open and close. Work complete for test.
542 BC 4 | Overload | Isolate & normalize supply
561 CP 1 | Service request: Isolate supply | Isolate & normalize supply
555 CP 3 | Alarm overload at CCR | Check at CP alarm overload fan motor, Reset. Alarm service and alarm DP oil filter. Inform production and mechanical to continue check.
555 CP 3 | Service request: Isolate supply | Isolate & normalize supply
555 CP 3 | Rental Comp -Cable incoming snap | Cut for 'vendor' to check compressor for futher action. Cable incoming has not been installed yet.
54A BM 1 | Troubleshoot | Replace socket 5 pin to 4 pin. lay cable for booster 30kw. Contactor service and cleaning 54 BM 1. Supervise contactor DC motor
54A BM 1 | Monitoring | Supervise VC and hand over by VC Motor
545 FM 2 | Alarm | Isolate & normalize supply
54A BM 1 | Insulation test | Test for Rotor-1kv - ohm. Stater- 5 kv-100m ohm. Cable- 5kv-800m ohm. Connect cable at GCB, compartment. Connect cable at terminat motor. On heater and add on extra heat rotor with spotlight.
54A BM 1 | Insulation Test | Topup water for starter 84 liter. Add heater blower 2 pcs. Insulation test rotor. R-E - 1 KV -0.5 M Ohm. Y-E- 1 KV-0.5 M Ohm. B-E-1 KV - 0.5 M Ohm. Follow up needed.
545 FM 2 | Alarm stop machine | Reset panel
561 CP 1 | Trip | Isolate & normalize supply
545 FM 2 | Flow not show. Alarm AL60 AD fail | Isolate & normalize supply
545 FM 2 | Flow not show. | Isolate & normalize supply
545 FM 2 | Flow not show | Isolate & normalize supply
545 FM 2 | Alarm AL/60 AD fail | Isolate & normalize supply

## C.Mill 3
Date | Equipment # | Issues | Resolution
2023-08-28 | 562 MW | Overload | Isolate & normalize supply
2023-09-14 | 552 RP 1/RP 2 | Service request: Isolate supply | Rack out VCB
2023-09-14 | 552 RP 1/RP 2 | Service request: Isolate supply | Rack out VCB
2023-08-25 | 51A GA S | Overload | Isolate & normalize supply
2023-08-25 | 520 BC 1 | Alarm return fault | Isolate & normalize supply
2023-08-25 | 520 GA 1 | Shaft snap | follow up needed
2023-08-25 | 520 SG 1 | Overload | Isolate & normalize supply
2023-08-28 | 535 BC 5 | Overload | Isolate & normalize supply
2023-09-07 | 535 BC 6 | Overload | Isolate & normalize supply
2023-09-07 | 535 BC 9 | Overload | Isolate & normalize supply
2023-08-29 | 535 BC 5 1 | Overload | Isolate & normalize supply
2023-09-05 | 540 SX 2 | Overload | Isolate & normalize supply
2023-09-14 | 545 FN 4 | Rack in ACB | Close ACB
2023-09-14 | 545 FN 4 | Rack out ACB | Open ACB
2023-09-08 | 54B AC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-09-08 | 54B AC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-09-08 | 54B AC 1 | Service request: Disconnect cable speed switch | Disconnect cable speed switch. Reset.
2023-08-31 | 550 FN 1 | Overload | Isolate & normalize supply
2023-09-02 | 552 BC 1 | Overload | Isolate & normalize supply
2023-08-28 | 552 BL 1 | Overload | Isolate & normalize supply
2023-09-11 | 552 BL 1 | Overload | Check coil motor at MCC. Restart.
2023-09-12 | 552 BL 1 | Overload | Isolate & normalize supply
2023-09-12 | 552 BL 1 | Overload | Isolate & normalize supply
2023-09-14 | 552 BL 1 | Overload | Isolate & normalize supply
2023-09-01 | 552 HT 1 | WO CE 786 - abnomal sound | Check and replace motor.
2023-08-25 | 552 RP 1 | Machine fault - starter not in high position | Isolate & normalize supply
2023-08-28 | 552 RP 1 | Alarm starter rods not in high position | Isolate & normalize supply
2023-09-14 | 552 RP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-09-14 | 552 RP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-08-25 | 552 SG 3 | Attendance info base portion | Replace new base an restart. Follow up needed.
2023-09-02 | 552 SG 3 | Overload | Isolate & normalize supply
2023-09-08 | 552 SG 3 | Overload | Isolate & normalize supply
2023-09-08 | 552 SG 3 | Overload | Isolate & normalize supply
2023-09-12 | 552 SG 3 | Overload | Isolate & normalize supply
2023-09-13 | 552 SG 3 | Overload | Isolate & normalize supply
2023-09-14 | 552 SG3 | Overload | Isolate & normalize supply
2023-08-29 | 555 BF3 1 | Overload | Isolate & normalize supply
2023-08-28 | 555 DY 1 | alarm cannot reset at panel (A09) | Isolate & normalize supply
2023-09-10 | 560 BC 1 | Overload | Isolate & normalize supply
2023-09-05 | 560 BF 3 | Overload | Isolate & normalize supply
2023-09-06 | 560 BF 3 | Overload | Isolate & normalize supply
2023-09-13 | 561 FN 2 | Maintenance routine | Top up 12 liter distill water for starter.
2023-09-06 | 561 PG 1 | Cannot moving - WO (EC791) | Replace valve
2023-09-09 | 561 RL 1 | Low pressure | Repair key way problem
2023-09-09 | 561 RL 1 | Alarm starter not in first step | Isolate & normalize supply
2023-09-14 | 561 RL 1 | Alarm starter not in first step | Isolate & normalize supply
2023-09-11 | 561 RL 4 | Alarm return fault at CCR | Tighten control cable at contector and aux contact
2023-09-01 | 561 RL IN 2 T 1 | WO CE 787 - Temp. fluctuate | Replace PT 101
2023-09-09 | 562 AD 1 | Alarm A25 | Isolate & normalize supply
2023-08-29 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-09-02 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-09-10 | 562 CP 1 | Fan motor overload | Isolate & normalize supply
2023-08-29 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-09-02 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-08-29 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-09-02 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-08-28 | 562 FN 1 | Overload | Isolate & normalize supply
2023-09-02 | 562 HT 1 | Service request | Service motor
2023-08-28 | 562 MW 3 | Overload | Isolate & normalize supply
2023-08-28 | 562 MW 1 | Gate not fully open at site. CCR open. | Adjust limit switch
2023-08-28 | CM3 | Trip | Isolate & normalize supply
2023-09-10 | CM3 | CM3 & CM4 running smoothly | Standby
2023-09-11 | CM3 : 1. 545 FN 14, 2. 545 FN 15, 3. 545 FN 16, 4. 545 SR 3, 5. 545 SR 1 , 6. 535 BC 4, 7. 552 BE 1, 8. 552 BE 2, 9. 542 BE 1, 10. 542 BE 2, 11. 550 FN 1, 12. 552 FN 2 | Maintenance routine | Greasing motor
2023-08-25 | Fire alarm | Alarm | Isolate & normalize supply
2023-09-13 | 1. 555 CP 3, 2. 552 CP 1 3. 552 CP 2, 4. 510 AC 1, 5. 545 FN 4, 6. 552 FN 1 | Maintenance routine | Greasing Motor
2023-09-13 | Gypsum weighfeeder | Calibration | Gypsum weighfeeder physical calibration done
2023-09-16 | 54B AC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-09-18 | 552 BC 2 | Service request: Isolate supply | Isolate & normalize supply
2023-09-18 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2023-09-18 | 552 BC 2 | Service request: Isolate supply | Isolate & normalize supply
2023-09-18 | 550 RF 2 | Overload | Isolate & normalize supply
2023-09-18 | T5481 | Material to cement silo temp - open loop | follow up needed
2023-09-20 | 545 BM 1 | C shift drive cannot start bush lifting fault | Alarm at Panel control motor for RR faulire. Try force camcon to up position but reached on step machinism stuck. check and found the steering lock not in position. Try manual stary from CCR.
2023-09-20 | 552 BL 1 | Overload | Isolate & normalize supply
2023-09-21 | 548 AC 1 | Check speed switch and ropeswitch | Check and replace speed switch and ropeswitch
2023-09-21 | T5481 | WO CE802 - open loop | Replace terminator
2023-09-22 | 560 BP 3 | Overload | Isolate & normalize supply
2023-09-22 | 5340 BP 2 | WO RE239 Overload- 0.75 kW | Check motor 1 phase missing - normal group continue replace motor space.
2023-09-25 | 545 FN 4 01 | Rack out ACB | Isolate & normalize supply
2023-09-25 | 560 BF 1 | Overload | Isolate & normalize supply
2023-09-25 | 510 BF 1 M02 | Overload | Isolate & normalize supply
2023-09-25 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2023-09-25 | 561 BC 3 | Overload | Isolate & normalize supply
2023-09-25 | 51A GA S | Copper tank damage, gear for limit switch problem | Calibrate close/open gate
2023-09-26 | 560 BF 3 | Cable snap | Rejoint. Start but still trip overload. Disconnect cable and dismantle motor.
2023-09-26 | 552 BL 1 | Overload | Isolate & normalize supply
2023-09-27 | 560 BF 3 01 | New Installation | Prepare motor
2023-09-27 | 560 BF 3 01 | New Installation | Replace motor
2023-09-27 | 561 BC 3 | Overload | Isolate & normalize supply
2023-09-28 | 560 BP 3 | New Installation | test free run without load clamp amp. R= 11.64 Y=11.54 B=11.64
2023-09-28 | 560 BF 3 | Contactor stuck | Service contactor
2023-09-28 | Drayer CM3 | Trip overload breaker (alarm A09) | Service aux contact. Restart
2023-09-29 | CM3 - Stack 7 | Service request: Tidy up cable analog | Tidy up cable analog
2023-09-30 | 535 BC 5 | Overload | Isolate & normalize supply
2023-10-01 | CM3 | Running smoothly | Standby
2023-10-01 | 561 RL 1 | Alarm starter first stop | Isolate & normalize supply
2023-10-02 | 561 RL 1 | High vibration DE and NDE motor | Replace 22 pcs c/brush due to short. S/C 184291. WO-129160.
2023-10-02 | 561 BC 3 | Overload | Isolate & normalize supply
2023-10-02 | 560 RF 1 | Control breaker trip | Return fault
2023-10-02 | 561 BC 3 | cable snap | Rejoint cable and restart
2023-10-02 | 570 FN 1 | Overload | Isolate & normalize supply
2023-10-02 | 561 RL 1 | NDE/DE vibration alarm | Replace IFM sensor
2023-10-02 | 570 FN 1 | Motor short | Disconnect cable motor. Follow up needed.
2023-10-04 | 535 BC 2 | Service request: Isolate supply | off MCCB
2023-10-04 | 535 BC 5 | Service request: Isolate supply | off MCCB
2023-10-04 | 535 BC 2 | Service request: Isolate supply | on MSSB
2023-10-04 | 535 BC 5 | Service request: Isolate supply | on MSSB
2023-10-04 | 545 FN 16 | Service request: Isolate supply | Rack out VCB
2023-10-04 | 552 RP 1 | Service request: Isolate supply | Rack out VCB
2023-10-04 | 552 RP 1 | Service request: Isolate supply | Rack out VCB
2023-10-04 | 540 BC 1 | Service request: Isolate supply | off MCCB
2023-10-04 | 540 BC 2 | Service request: Isolate supply | off MCCB
2023-10-04 | 510 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-04 | 510 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-04 | 552 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-04 | 552 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-04 | 552 RP 1 M01 | Maintenance routine | Check carbon/brush, s/ring and starter
2023-10-04 | 552 RP 1 M02 | Maintenance routine | Check carbon/brush, s/ring and starter
2023-10-04 | 545 FN 16 | Maintenance routine | Check carbon/brush, s/ring and starter
2023-10-04 | 552 BL 2 | Check and test motor free run. | Test free run
2023-10-04 | 510 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-04 | 510 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 545 BM 1 | Service request: Isolate supply | Rack out GCR
2023-10-05 | 545 FN 4 | Service request: Normalize fuse form | Normalize fuse form
2023-10-05 | 545 SR 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 561 BC 3 | Overload | Isolate & normalize supply
2023-10-05 | 565 CP 3 | Service request: Isolate supply | Rack out ACB
2023-10-05 | 542 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 540 BC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 535 BC 4 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 552 RP 1 | Service request: Isolate supply | Rack in VCB
2023-10-05 | 552 RP 2 | Service request: Isolate supply | Rack in VCB
2023-10-05 | 545 BM 1 | Maintenance routine | Check brush lifting compartment and starter
2023-10-05 | 520 GA 1 01 | Service request: check gate | Adjust limit switch
2023-10-05 | 545 FN 4 01 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 545 FN 16 01 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 552 BE2 01 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 552 BE 01 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 535 BC2 01 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 535 BC5 01 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | CM3 | cable snap | Rejoint cable and restart
2023-10-05 | 540 BC 2 | alarm motion | Check and found base speed. Switch loose. Adjust & tighten bolt & nut. Restart.
2023-10-05 | 540 WF 1 | alarm CCP | Check & found emergency switch bad contact. Service & restart.
2023-10-05 | 545 FM 2 | AL10 alarm flow high | Isolate & normalize supply
2023-10-05 | 535 BC 4 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 540 BC 1 | alarm not ready | breakers supply off. Restart.
2023-10-05 | 54B AC 1 | Isolate supply req by Mech. | off MCCB - work done
2023-10-06 | 555 DY 1 | Alarm AO9 | Check found overload breaker trip. Reset.
2023-10-06 | 552 HT 1 | Alarm return fault at CCR | Check found aux contact running. (Return) damage replace. Restart.
2023-10-06 | 561 CP 1 | Trip by alarm element outlet temp. | Isolate & normalize supply
2023-10-07 | 552 SG 3 | Overload | Isolate & normalize supply
2023-10-09 | 561 TR 1 | Maintenance routine | Transformer inspection
2023-10-09 | 54A TR 1 | Maintenance routine | Transformer inspection
2023-10-09 | 54B TR 1 | Maintenance routine | Transformer inspection
2023-10-09 | 545 TR 1 | Maintenance routine | Transformer inspection
2023-10-09 | 552 TR 1 | Maintenance routine | Transformer inspection
2023-10-09 | 545 BM 1 | Operate motor | Isolate & normalize supply
2023-10-09 | 510 BF 2 | Overload | Isolate & normalize supply
2023-10-09 | 54B AC 1 | Not ready | Isolate & normalize supply
2023-10-09 | 510 BF 2 | Overload | Isolate & normalize supply
2023-10-09 | 54B AC 1 | Not ready | Isolate & normalize supply
2023-10-10 | 562 CP 1,2,3 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 561 BC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 561 BC 4 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 54A BC 2 | Overload | Isolate & normalize supply
2023-10-10 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 561 BC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 561 BC 4 | Overload | Isolate & normalize supply
2023-10-10 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 562 CP 1 | Overload motor | Isolate & normalize supply
2023-10-10 | 562 CP 2 | Elemet outlet | Isolate & normalize supply
2023-10-11 | 55A BM 1 | Insulation test | Test for motor and starter at CM1 main drive
2023-10-11 | 510 BF 1 M02 | Overload | Isolate & normalize supply
2023-10-11 | 545 FM 1 01 | Alarm | Isolate & normalize supply
2023-10-11 | 55A BM 1 | Maintenance routine | Blow dust and install heater
2023-10-12 | 561 PG 1 | WO CE 819 - Alarm run line | Service sensor. Tighten cable.
2023-10-12 | 552 SG 3 | Overload | Isolate & normalize supply
2023-10-13 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-13 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-13 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-10-13 | 561 WP 1 FY 1 FII (Flow control gate) | Control Valve (water) cement Mill 4 cannot control auto at CCR. | Replace positioner gate
2023-10-13 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-13 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-13 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-10-14 | 555 DY 1 | Contactor stuck | Replace contactor
2023-10-15 | CCR 2 | PC Cement Mill 3 blank | Rejoint loose cable
2023-10-15 | 552 RP 1 | Maintenance routine | HT Motor Monitoring
2023-10-15 | 552 RP 2 | Maintenance routine | HT Motor Monitoring
2023-10-15 | 545 FN 16 | Maintenance routine | HT Motor Monitoring
2023-10-15 | 546 BM 1 | Maintenance routine | HT Motor Monitoring
2023-10-15 | 561 FN 2 | Maintenance routine | HT Motor Monitoring
2023-10-15 | 561 RL 1 | Maintenance routine | HT Motor Monitoring
2023-10-15 | 561 CL 4 T03 | Classifier lower bearing temp fluctuate | Tighten cable at terminat block. Start back still trip.(fluctuate) during start feed. Trace and suspect joint cable fault.(intermittent) cut and connect back at joint box. Restart.
2023-10-15 | 562 CP 2 | Alarm element outlet temp | Isolate & normalize supply
2023-10-16 | 55A BM 1 | Insulation Test | Stator 0 ohm. Direct short prepare new heater
2023-10-16 | 545 BM 1 | Insulation Test | Spare motor - Starter - 100 mn
2023-10-16 | 561 FN 4 | control breaker trip | Isolate & normalize supply
2023-10-16 | 550 DY 1 | Trip by alarm 409 (overload breaker) | Isolate & normalize supply
2023-10-16 | 550 DY 1 | Alarm A25 "high temp" time starting foam compressor activation not active in standby | Suspect contactor fault. Contactor 24V ac No spare. Check at w/shop found contactor 42V same model swapcoil test ok. Work done
2023-10-17 | 55A BM 1 | Insulation Test | Continue check still short add 1 heater.
2023-10-18 | 55A BM 1 | Insulation Test | Insulation test still short
2023-10-18 | 561 RL 1 | short | Replace 12 pcs c/brush
2023-10-19 | 555 CP 3 | Service request: Isolate supply | Open ACB
2023-10-19 | 55A BM 1 | Insulation Test | Motor stator - still short. Motor cable - 3.5 ohm
2023-10-19 | 540 WF 2 | Maintenance routine | Physical calibration
2023-10-21 | 562 AD 1 | Alarm A25 | Isolate & normalize supply
2023-10-21 | 561 BC 4 | Alarm motion detector | Check and found speed switch out of position. Adjust speed swirch and test ok. start back system.
2023-10-21 | 510 AC 1 | Overload | Isolate & normalize supply
2023-10-23 | 55A BM 1 | Insulation Test | Run motor.
2023-10-23 | 545 BM 1 | Insulation Test | Spare motor
2023-10-23 | 552 SG 3 | Overload | Isolate & normalize supply
2023-10-23 | 552 VV 1 | Breaker control trip | Isolate & normalize supply
2023-10-24 | 545 BM 1 | Service request: Tidy up cable | Spare motor clean water inside motor. Tidy up cable at CM3
2023-10-25 | 545 BM 1 | Service request: Tidy up cable | Tidy up cable
2023-10-26 | 561 RL 1 | Sparking | Check carbon brush
2023-10-26 | 561 BC 4 | WO CE 628 -Local switch not function | Replace local switch
2023-10-26 | 535 BC 5 | Overload | Isolate & normalize supply
2023-10-26 | 561 AL 1 | Rotor short to earth | Dismantle motor
2023-10-26 | 561 RL 105 | Troubleshoot | Disconnect cable & dismantle rotor inching.
2023-10-27 | 54 BC 2 | Overload | Isolate & normalize supply
2023-10-29 | 552 LQ2 TZ2 T02 | Temp. fluctuate | Check found cable loose at PT100. Tighten cable.
2023-10-29 | 561 CP 1 | Miller req to check alarm not ready | Isolate & normalize supply
2023-10-29 | 561 RL 105 | Motor Testing | Run motor.
2023-10-29 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-30 | 561 RL 1 (Hyundai) | Motor Testing | Test motor main drive. Free run couple, 100 - 110 kw. 80 Amp / 79 Amp/ 81 Amp
2023-11-02 | 550 RF 2 | Overload | Isolate & normalize supply
2023-11-04 | 561 GR 1 M01 TR05 | Oil pressure low | Check found key master loose. Disconnect cable motor. Repair key motor.
2023-11-04 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2023-11-04 | 540 WF 2 01 | Alarm belt not feedback | Cannot reset. Req miller to call and check first. Try local. Alarm clear. Restart.
2023-11-05 | 561 GR 1 M01 TP05 | Disconnect cable motor | Mech repair welding shaft motor p-up. Rejoint cable & test run.
2023-11-05 | 561 CP 1 | Alarm almost collect | Isolate & normalize supply
2023-11-05 | 562 CP 1 | Fan motor overload | Isolate & normalize supply
2023-11-05 | 561 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-11-05 | 561 GR 3 | Gear recover oil pressure low | Replace 1 pc solenoid valve (No.11). Solenoid valve Part No: DG4V-5-31B-M-PL-D-6-49
2023-11-05 | 562 GR 3 | gear recover oil pressure low | Replace 1 pc solenoid valve. Try start system & monitor, Work together with EE Haziruddin, EE Ikmal, Saifuddin. Solenoid valve part No: DG5V-H8-2A-P2-D-86-JA.
2023-11-05 | 563 GR 3 | Trip | Trip again with same alarm after mill running about 1 hour. * 561 GR01 TP5. *561 GR03M01 P43
2023-11-06 | 561 GR 1 TP05 | Troubleshoot | Check found welding crack dismantle motor to w/shop for modification. Modification by Machinist feedback and test ok.
2023-11-06 | 561 GR 3 | Troubleshoot | Gear reducer pump
2023-11-06 | 561 GR 1 TP05 | CM4 | Dismantle and install back motor. Modification motor & pump shaft.
2023-11-07 | 552 RP 1 M01 | Maintenance routine (CNY 2024 stoppage) | Monitor for bearing replacing on CNY stopage. Motor c/brush, s/ring and starter for the following motor.
2023-11-07 | 552 RP 1 M02 | Maintenance routine (CNY 2024 stoppage) | Monitor for bearing replacing on CNY stopage. Motor c/brush, s/ring and starter for the following motor.
2023-11-07 | 545 FN 16 | Maintenance routine (CNY 2024 stoppage) | Monitor for bearing replacing on CNY stopage. Motor c/brush, s/ring and starter for the following motor.
2023-11-07 | 545 BM 1 | Maintenance routine (CNY 2024 stoppage) | Monitor for bearing replacing on CNY stopage. Motor c/brush, s/ring and starter for the following motor.
2023-11-07 | 561 FN 2 | Maintenance routine (CNY 2024 stoppage) | Monitor for bearing replacing on CNY stopage. Motor c/brush, s/ring and starter for the following motor.
2023-11-07 | 561 RL 1 | Maintenance routine (CNY 2024 stoppage) | Monitor for bearing replacing on CNY stopage. Motor c/brush, s/ring and starter for the following motor.
2023-11-07 | 552 W 1 | Alarm key not auto | Check cable joint ok. Suspect local switch. Replace local switch ok. After a few minutes miller alarm, trace found cable snape. Cable no 1 and u joint back test ok.
2023-11-09 | 590 VF 1 | New Installation | Vibrating Feeder - Crusher China - Install spare motor and new base. WO CE 843.
2023-11-10 | 552 BI 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-10 | 552 BI 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-10 | 545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-11 | 543 BM 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-11 | 560 FN 1 | Overload | Isolate & normalize supply
2023-11-11 | 561 CP 2 | Alarm overload at CCR | Check at CP alarm service required. Check status alarm DP oil separator service max 0.80 bar. Reset
2023-11-12 | 545 FN 4 01 | Service request: Isolate supply | Isolate & normalize supply
2023-11-12 | 545 FN 16 01 | Service request: Isolate supply | Isolate & normalize supply
2023-11-12 | 545 SR 1 01 | Service request: Isolate supply | Isolate & normalize supply
2023-11-12 | 545 SR 3 01 | Service request: Isolate supply | Isolate & normalize supply
2023-11-12 | 545 BM 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-12 | 562 CP 1 | Overload fan motor | Isolate & normalize supply
2023-11-12 | 562 CP 3 | Element outlet temp. high | Isolate & normalize supply
2023-11-13 | 552 RP 1 | Maintenance routine | Check c/brush - Blow motor, starter and carbon dust at s/ring compartment
2023-11-13 | 552 RP 2 | Maintenance routine | Check c/brush and s/ring condition. Blow motor, starter and carbon dust at s/ring compartment. Replace 2 pcs c.brush
2023-11-13 | 545 FN 16 | Maintenance routine | Check c/brush and s/ring condition. Blow motor, starter and carbon dust at s/ring compartment. Replace 5 pcs c.brush
2023-11-13 | 545 FN 16 | Service request: Isolate supply | Isolate & normalize supply
2023-11-13 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2023-11-14 | 545 SR 3 | Troubleshoot | Connect motor cable and tested
2023-11-14 | 561 RL 1 | Troubleshoot | Fit back cooling Fan ( Old motor)
2023-11-14 | 545 SR 3 01 | Service request: Isolate supply | Isolate & normalize supply
2023-11-14 | 545 SR 1 01 | Service request: Isolate supply | Isolate & normalize supply
2023-11-14 | 545 BM 1 | Alarm not ready | Rack in back
2023-11-14 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-17 | 552 PG 2 | WO :CE849 Alarm runtime after select to open | Check and found soleniod valve problem. Replace soleniod valve.
2023-11-18 | 552 PG 2 | WO :CE850 Alarm runtime after mech replace pneumatic Actuators valve | Check and found soleniod valve problem. Replace soleniod valve.
2023-11-18 | 550 FN 1 01 | Overload | Isolate & normalize supply
2023-11-19 | 555 AL 1 | WO CE851 Blow tank B not discharge | Replace pressure switch
2023-11-19 | 562 CD 1 01 | Service request: Isolate supply | Isolate & normalize supply
2023-11-19 | 562 CP 2 01 | Service request: Isolate supply | Isolate & normalize supply
2023-11-19 | 562 CP 3 01 | Service request: Isolate supply | Isolate & normalize supply
2023-11-19 | T5476 | Show open loop | Tighten cable t/c
2023-11-19 | 562 CP 1 01 | Service request: Isolate supply | Isolate & normalize supply
2023-11-19 | 562 CP 2 01 | Service request: Isolate supply | Isolate & normalize supply
2023-11-19 | 562 CP 3 01 | Service request: Isolate supply | Isolate & normalize supply
2023-11-19 | 561 GR 3 01 | Service request: Isolate supply | Isolate & normalize supply
2023-11-20 | 561 BF 02 | Service request: Isolate supply | Isolate & normalize supply
2023-11-20 | 562 CP 01 | Element out let temp high 120 C | Isolate & normalize supply
2023-11-20 | 552 RP 1 | Monitoring | HT Motor Monitoring for the following motor
2023-11-20 | 552 RP 2 | Monitoring | HT Motor Monitoring for the following motor
2023-11-20 | 545 FN 14 | Monitoring | HT Motor Monitoring for the following motor
2023-11-20 | 545 BM 1 | Monitoring | HT Motor Monitoring for the following motor
2023-11-20 | 561 FN 2 | Monitoring | HT Motor Monitoring for the following motor
2023-11-20 | 561 RL 1 | Monitoring | HT Motor Monitoring for the following motor
2023-11-21 | 542 BE 1 | Isolate supply req by mech. | off MCCB
2023-11-21 | 561 RL 1 | Maintenance routine (CNY 2024 stoppage) | Monitor and survey motor for bearing replacement on CNY
2023-11-21 | 552 CP 2 | Trip | Isolate & normalize supply
2023-11-22 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-22 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-11-22 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-22 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-22 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-11-22 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-22 | 561 FN 2 | Short | Replace 8 pcs c/brush. Top up 12 liter distill water for starter. Top up 12 liter distill water for starter.
2023-11-22 | 561 RL 1 | Maintenance routine | Top up 24 liter distill water for starter
2023-11-22 | 561 DA 2 | cable snap | Rejoint cable and restart
2023-11-23 | 54A BM 1 | Insulation test | Inject 6kv - 0 ohm. Inject 1kv - 8 ohm
2023-11-23 | 545 BM 1 | Insulation test | Inject 6kv - 60 ohm. Inject 1kv - 100 ohm
2023-11-23 | 550 CP 1 | Control voltage fuse blow | replace control voltage fuse
2023-11-24 | 562 PP 1 | Valve not function | Replace and service valve
2023-11-24 | 562 CP 2 | Breaker F12 trip | Isolate & normalize supply
2023-11-24 | 552 RP 1 | Reset F12 trip | Isolate & normalize supply
2023-11-25 | 535 BC 6 | Overload | Isolate & normalize supply
2023-11-25 | 550 FN 1 | Overload | Isolate & normalize supply
2023-11-26 | 555 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-26 | 550 FN 1 | Overload coloum 24v error | Replace inverter
2023-11-26 | 550 FN 1 | Schneider panel problem | Change & install back card old panel & spare panel
2023-11-27 | 562 PP 1 | Service request: Check Blow tank A | Check valve. Check pipe. Suspect blockage
2023-11-27 | 555 AL 1 01 | Blow tank A not function | Check valve. Check found cable coil valve snap. Repair & test.
2023-11-28 | 540 SX 2 | Overload | Isolate & normalize supply
2023-11-28 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-28 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-11-28 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-29 | 552 VV 2 | Alarm run time | Check and found limit switch. Stuck. Service & test.
2023-11-29 | 545 FM 2 | AL 10 flow to high | Isolate & normalize supply
2023-11-30 | 561 RL 1 | Alarm mill liquid starter first step | Isolate & normalize supply
2023-11-30 | 561 RL 1 | Alarm state first step | Isolate & normalize supply
2023-12-02 | 535 BC 6 | Overload | Isolate & normalize supply
2023-12-02 | 552 CP 2 | Trip | Isolate & normalize supply
2023-12-03 | 552 RP 1 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
2023-12-03 | 552 RP 2 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
2023-12-03 | 545 FN 16 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
2023-12-03 | 545 BM 1 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
2023-12-03 | 561 RL 1 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
2023-12-03 | 561 FN 2 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
2023-12-03 | 540 SX 2 | Overload | Isolate & normalize supply
2023-12-03 | 540 BC 1 | Overload | Isolate & normalize supply
2023-12-03 | 540 BC 1 | Alarm motion detector | Check and found speed switch out of position. Calibrate
2023-12-04 | 555 BF 3 | Overload | Isolate & normalize supply
2023-12-04 | 545 FM 2 | AL10 flow too high | Isolate & normalize supply
2023-12-04 | 552 CP M02 | Overload | Isolate & normalize supply
2023-12-05 | 535 BC 4 | Maintenance routine | Greasing the following motor
2023-12-05 | 552 FN 1 | Maintenance routine | Greasing the following motor
2023-12-05 | 552 FN 2 | Maintenance routine | Greasing the following motor
2023-12-05 | 552 BE 1 | Maintenance routine | Greasing the following motor
2023-12-05 | 552 BE 2 | Maintenance routine | Greasing the following motor
2023-12-05 | 542 BE 1 | Maintenance routine | Greasing the following motor
2023-12-05 | 542 BE 2 | Maintenance routine | Greasing the following motor
2023-12-05 | 555 CP 3 | Maintenance routine | Greasing the following motor
2023-12-05 | 552 CP 1 | Maintenance routine | Greasing the following motor
2023-12-05 | 552 CP 2 | Maintenance routine | Greasing the following motor
2023-12-06 | 561 RL 1 | Service request: Isolate supply | Rack out GBC
2023-12-06 | 561 BC 3 | Overload | Isolate & normalize supply
2023-12-06 | 561 BC 3 | Cable speed switch snap (220V) | Rejoint cable and restart
2023-12-06 | 561 CR 2 | Alarm overload at CCR | Check at status DP air filter alarm reset
2023-12-06 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2023-12-06 | 560 BC 3 | Open coil | Check motor. Prepare for motor replacement.
2023-12-06 | 560 BC 3 01 | Install motor and install new motor | Test run local
2023-12-07 | 560 BC 3 | Service request: Isolate supply | Isolate & normalize supply
2023-12-08 | CM1 | Cable from PL1 to CM1 transformer | Check & megger cable.
2023-12-08 | 535 B 6 | Overload | Isolate & normalize supply
2023-12-11 | 552 LQ 3 01 | Not show flow at CCR | Check found coil socket snap and 1 cable snap. Replace new socket and cut joint back . Test run -ok
2023-12-11 | Stack 7 | Check at monitor alarm not response | Off and back supply to auto calibrate. Reading at 6.35
2023-12-12 | 561 FN 2 M01 | Troubleshoot | To replaced 3 pcs c/brushes
2023-12-12 | 562 PP 1 | Troubleshoot | Change s/valve
2023-12-12 | 562 PP 2 | Troubleshoot | Change s/valve
2023-12-12 | 555 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 560 BC 1 | Troubleshoot | Load cell prebin
2023-12-12 | 561 BC 1 | Motor abnormal sound | Check test run
2023-12-12 | 555 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 545 FM 2 | AL10 flow too high | Isolate & normalize supply
2023-12-12 | 552 LC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 561 CP 02 | Alarm Dp air filter | Isolate & normalize supply
2023-12-12 | 562 CP 01 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 562 CP 02 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 562 CP 03 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 560 BC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 550 RF 2 | Overload | Isolate & normalize supply
2023-12-12 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 562 CP 1 | Overload from motor | Isolate & normalize supply
2023-12-13 | 552 RP 1 | Maintenance routine | Check carbon brush
2023-12-14 | 561 CP 2 | Breaker for cooling fan damage | Replace breaker
2023-12-14 | 561 CL A1 | Local switch pole broken | Check found local switch pole broken. Repair.
2023-12-14 | 560 BE 1 | Alarm motion | Check found control breaker 220V Q148 trip reset.
2023-12-15 | 555 CP 3 | Alarm at temp | Isolate supply and normalize supply
2023-12-16 | 560 BF 3 01 | Overload | Isolate & normalize supply
2023-12-16 | 535 BC 5 01 | Overload | Isolate & normalize supply
2023-12-16 | 542 BC 4 | Overload | Isolate & normalize supply
2023-12-16 | 561 CP 1 | Overload | Isolate & normalize supply
2023-12-16 | 561 CP 2 | Can't start from CCR | Maintenance fault. Found CP in local mode. Change to remote.
2023-12-17 | 561 CP 2 | Overload fan motor | Isolate & normalize supply
2023-12-19 | 561 PG 1 | WO CE868 Alarm runtime | Check and found solenoid valve problem. Replace solenoid valve and test manual open & close.
2023-12-20 | 555 CP 3 | Service request: Isolate supply | Isolate supply and normalize supply
2023-12-21 | 552 CP 1 | Fault soft start | Isolate supply and normalize supply
2023-12-21 | Stacker Cement Mill | Cannot start | Check and found breaker 220V trip. MCCB 6. Trip cannot reset.Belt cannot reset. Suspect cable short. Follow up needed.
2023-12-22 | 510 GA 3 | Overload | Isolate & normalize supply
2023-12-22 | 510 BA 3 | Overload | Isolate & normalize supply
2023-12-23 | 555 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-12-23 | 545 FM 2 | AL10 flow to figh | Isolate & normalize supply
2023-12-24 | 535 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-12-25 | 552 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2023-12-25 | 552 BE 1 MO2 | Overload | Isolate & normalize supply
2023-12-26 | 545 BC 1 | Overload | Isolate & normalize supply
2023-12-26 | 545 RF 1 | Overload | Isolate & normalize supply
2024-12-28 | 561 RL 1 | Rack in GCB | Isolate & normalize supply
2024-12-28 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2024-12-31 | 535 BC 3 | Overload | Isolate & normalize supply
2024-12-31 | 535 BC 6 | Overload | Isolate & normalize supply
2024-01-01 | 552 RP 1 | Monitoring | HT Motor monitoring, motor c/brush, s/ring and starter condition.
2024-01-01 | 552 RP 2 | Monitoring | HT Motor monitoring, motor c/brush, s/ring and starter condition.
2024-01-01 | 545 FN 16 | Monitoring | HT Motor monitoring, motor c/brush, s/ring and starter condition.
2024-01-01 | 545 BM 1 | Monitoring | HT Motor monitoring, motor c/brush, s/ring and starter condition.
2024-01-01 | 561 FN 2 | Monitoring | HT Motor monitoring, motor c/brush, s/ring and starter condition.
2024-01-01 | 561 RL 1 | Monitoring | HT Motor monitoring, motor c/brush, s/ring and starter condition.
2024-01-03 | CM1 | Service request: Isolate supply | Rack in GCB
2024-01-03 | CM3 ER 7 | Trip incoming VCB | Close VCB
2024-01-03 | CM1 | Insulation test | Test for transformer. R-E: 700, Y-E: 700, B-E: 700
2024-01-03 | CM2 | cable punctured | Incoming Line 1 trip at MTS. Connect cable and normalize supply. Check and found cable CM1 transformer punctured behind CM2 w/feeder room.
2024-01-03 | CM3 | Insulation test | Test for transformer. R-E: 1.4 ohm, Y-E: 1.4 ohm, B-E: 1.4 ohm
2024-01-03 | CM4 | Insulation test | Test for cable main drive. R-E: 100 ohm, Y-E: 50 ohm, B-E: 25 ohm, R-Y: 14 ohm, R-B: 14 ohm, Y-B: 16 ohm
2024-01-03 | 545 FM 1 | AL10 flow to high | Isolate & normalize supply
2024-01-04 | 590 VF 1 | Motor Testing | To test motor. Motor rated 22A (hopper empty) R-38 A, Y-37.9 A, B-38 A
2024-01-04 | 590 VF 1 | Try release spring tension and test | R-30 A, Y-30.2 A, B-30.5 A
2024-01-04 | 590 VF 1 | Troubleshoot | Reposition motor and modified base motor test. R-21.5 A, Y-21.7 A, B-22 A
2024-01-04 | 590 VF 1 | Gearbox problem | R-23 A, Y-23 A, B-23 A. After few minute motor trip on 23 A O/L setting 24A. To be continue test due to 590 BC 1 gear box problem. Disconnect cable motor 590 BC 1
2024-01-05 | 542 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-01-05 | 54A FA 2 | Overload | Reset still not ok, Check and weight motor amp old ohm same. Check motor bearing stuck. Motor dismantle and already to workshop.
2024-01-06 | 54A FA 2 | New Installation | Install coupling at new motor. Install motor connect cable alignment. Test rotation and pleasure amp.
2024-01-06 | 54A FA 2 | Trip alarm A28 | Silo 1-1. Assist group shift to install motor
2024-01-08 | 562 AD 1 M01 | Trip alarm A28 | Isolate & normalize supply
2024-01-08 | 561 FN 2 | short | Check c/brush. Top up 20 liter distill water for starter due to low level.
2024-01-08 | 561 RL 1 | maintenance routine | Check c/brush , s/ring and starter
2024-01-08 | 590 VF 1 | Test run | R-25.5, Y-25.5 , B-25.5
2024-01-08 | 590 VF 1 | After release spring | R-23.5, Y-23.5 , B-23.5
2024-01-08 | 590 VF 1 | motor overheat | Test free run 16A. Motor rated 22A.
2024-01-09 | 552 GA 1 | gate stuck | Isolate & normalize supply
2024-01-09 | 545 BM 1 | Insulation test | Test for spare motor. Starter R-E: 70 ohm, Y-E: 70 ohm, B-E: 70 ohm
2024-01-09 | 545 BM 1 | Insulation test | Test for spare motor. Starter R-E: 12 ohm, Y-E: 12 ohm, B-E: 12 ohm
2024-01-10 | 54 LP1 M01 | Insulation low and bearing jammed. | Service HEMT winding
2024-01-10 | 545 BM 1 | Motor Testing | Spare motor prepare space to relocate motor at warehouse.
2024-01-10 | 562 CP 1 | Overload fan motor | Isolate & normalize supply
2024-01-10 | 562 CP 1 01 | Isolate supply | Off MCCB
2024-01-10 | 562 CP 2 01 | Isolate supply | Off MCCB
2024-01-10 | 562 CP 3 01 | Isolate supply | Off MCCB
2024-01-11 | 510 AC 1 | Overload | Isolate & normalize supply
2024-01-11 | 510 AC 1 | Service request: Isolate supply | Isolate & normalize supply
2024-01-15 | CM1 | Transformer insulation test. | R: 900 ohm, Y: 900 ohm, B: 900 ohm
2024-01-15 | CM1 | Insulation test | Test for cable. R-E: 30 ohm, Y-E: 140 ohm, B-E: 100 ohm. Rejoint cable.
2024-01-15 | 54A LP 1 M01 | New Installation | Reassemble motor. Replace 2 pcs bearing 6205 ZZ. Test run. R: 1.4 A, Y: 1.4 A, B: 1.5A. Motor 1.1 KW.
2024-01-15 | 561 RL 1 M01 | Service request: Isolate supply | Isolate & normalize supply
2024-01-15 | 562 CP 1 | Overload fan motor | Isolate & normalize supply
2024-01-17 | CM1 | Insulation test | Test for transformer. R-E: 1 ohm , Y-E: 1 ohm, B-E: 1 ohm
2024-01-17 | CM1 | cable punctured | 4 meter from join. Connect back supply from CM2 to CM1. Rack out incoming ACB CM1.
2024-01-17 | 545 BM 1 | Insulation test | Test for spare motor.
2024-01-17 | 535 BC 6 | Overload | Isolate & normalize supply
2024-01-18 | 552 RP 1 | maintenance routine | Check motor , carbon brush, s/ring and starter
2024-01-18 | 552 RP 2 | maintenance routine | Check motor , carbon brush, s/ring and starter
2024-01-19 | CM3 | WO: CE 879 : Miller request to check group. Group 545 and 535 trip. | Check at ER5 trip incoming. Check and found breaker for 545 FN 13 trip. Perform insulation test at terminal, result show motor short. Replace motor and test.
2024-01-19 | 545 FN 13 | Motor short | 15KW, 4 pole, 27.5 A. Taken record motor at workshop for replacement test run with fan. R-19-5 A, Y-19-5 A, B-19-4 A. Hand over to planner for alignment.
2024-01-19 | 550 FN 1 | New Installation | Install stopper and alignment panel inverter.
2024-01-21 | 552 BC 4 | Overload | Isolate & normalize supply
2024-01-22 | 552 RP 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-01-22 | 552 RP 2 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-01-22 | 545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-01-22 | 545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-01-22 | 561 FN 2 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-01-22 | 561 RL 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-01-22 | 542 BC 4 | Monitoring | Remonitoring LV Motor for bearing replacement on CNY.
2024-01-22 | 520 BC 8 | Monitoring | Remonitoring LV Motor for bearing replacement on CNY.
2024-01-22 | 550 BF 3 | Monitoring | Remonitoring LV Motor for bearing replacement on CNY.
2024-01-23 | 562 CP 1 | Isolate supply | Isolate & normalize supply
2024-01-23 | 562 CP 2 | Isolate supply | Isolate & normalize supply
2024-01-23 | 562 CP 3 | Isolate supply | Isolate & normalize supply
2024-01-23 | 561 CP 1 | Alarm | Isolate & normalize supply
2024-01-23 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-01-23 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-01-23 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-01-25 | 562 CP 1 | Overload from motor | Isolate & normalize supply
2024-01-28 | 562 AD 1 M01 | Alarm A25 | Isolate & normalize supply
2024-01-29 | 55 B1 T1 | GCB always closing | Service
2024-01-29 | 545 BM 1 | Insulation test | Test for spare motor. Stator - R-E: 70 M ohm, Y-E: 70 M ohm, B-E: 70 M ohm
2024-01-29 | 545 BM 1 | Insulation test | Test for spare motor. Rotor - R-E: infiniti, Y-E: infiniti, B-E: infiniti
2024-01-29 | 55B 1T1 | GBC cannot tripping | Replace tripping coil for 55B 1T1 (CM2)
2024-01-29 | 562 CP 1 | Overload fan motor | Isolate & normalize supply
2024-01-29 | 561 CP 1 | Return fault at CCR | Check at Panel CP alarm starter feedback contact. Reset. Restart still return fault. Contactor not energize. Indicator " Comp run" at controller showing run. Attendant check oil leak. Try local motor still not run. Suspect safety sensor out off or controller problem. Need to follow up - trip.
2024-01-30 | 561 CP 2 | Not load | Disconnect, cut & rejoint cable.
2024-01-30 | 545 FN 4 | Isolate supply | Isolate & normalize supply
2024-01-30 | 545 FN 20 | Isolate supply | Isolate & normalize supply
2024-01-30 | 545 BM 1 | Isolate supply | Isolate & normalize supply
2024-01-30 | 561 BC 1 | Isolate supply | Isolate & normalize supply
2024-01-30 | 561 BC 4 | Isolate supply | Isolate & normalize supply
2024-01-30 | 552 FN 2 | Not ready | Isolate & normalize supply
2024-01-31 | 561 BC 4 | Overload | Isolate & normalize supply
2024-01-31 | 561 CP 2 | Socker valve problem | Repair socker valve
2024-01-31 | 562 AD 1 | Alarm 411, A09 | Isolate & normalize supply
2024-01-31 | 561 CP 1 | open switch | By pass temp switch
2024-01-31 | 54A BM 1 |  | Lay cable (fly) from MCC CM1, to main drive motor and to winding motor for heating. Motor already baricate. Amp - R-3.2A. Y-3.2A, B-3.2A.
2024-01-31 | 550 RF 2 | Overload | Isolate & normalize supply
2024-01-31 | 562 AD 1 M01 | Dryer alarm A25 | Isolate & normalize supply
2024-02-01 | 552 RP 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-02-01 | 552 RP 2 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-02-01 | 545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-02-01 | 545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-02-01 | 561 FN 2 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-02-01 | 561 RL 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-02-01 | 552 RP 1 | short | Replace 1 pc carbon brush
2024-02-01 | 562 AD 1 | Service request: Dryer check. Alarm A25 | Off & restart Dryer. Test ok
2024-02-01 | 552 CP 2 | Overload | Isolate & normalize supply
2024-02-02 | 54 A BM 1 | Insulation test | Insert 6KV R-E- 0 M ohm, Y-E- 0 M ohm , B-e- 0 M ohm
2024-02-02 | 54 A BM 1 | Insulation test | Insert 1 KV R-E- 15 M ohm, Y-E- 15 M ohm , B-E- 15 M ohm
2024-02-03 | 552 RP 1 | CE 885. Return fault | Check at panel VCB trip. Check motor found carbon crush sparking. Rack out VCB. Dismantlr carbon brush and holder. Megger : stator. Normal group continue skin slip ring-inprogress.
2024-02-03 | 552 RP 1 | Roller press motor CM3 | Checking motor.
2024-02-03 | 552 RP 1 | Roller press motor CM3 | Motor stationary site failure suspect carbon brush stuck holder cause sparking on slip ring.
2024-02-03 | 552 RP 1 | Monitoring | Visual inspection
2024-02-04 | 552 RP 1 | short | Check carbon brush and ring on stationary motor. Replace 1 pc carbon brush on movable motor
2024-02-04 | 552 RP 1 | short | Replace 1 pc carbon brush on movable motor
2024-02-05 | 552 RP 1 | Maintenance routine | Greasing motor
2024-02-05 | 552 RP 2 | Maintenance routine | Greasing motor
2024-02-05 | 561 FN 1 | Maintenance routine | Greasing motor
2024-02-05 | 561 FN 2 | Maintenance routine | Greasing motor
2024-02-05 | 561 RL 1 | Maintenance routine | Greasing motor
2024-02-05 | 561 CLA 1 | Maintenance routine | Greasing motor
2024-02-05 | 560 FN 1 | Maintenance routine | Greasing motor
2024-02-05 | 561 FN 3 | Maintenance routine | Greasing motor
2024-02-05 | 561 RL 1 03 | Maintenance routine | Greasing motor
2024-02-05 | 552 RP 1 | Maintenance routine | Check carbon brush & slip ring condition
2024-02-05 | 552 RP 2 | Maintenance routine | Check spring tension, carbon brush loosenes & starter condition
2024-02-06 | 561 TR 1 | Monitoring | Transformer inspection
2024-02-06 | 54A TR 1 | Monitoring | Transformer inspection
2024-02-06 | 54B TR 1 | Monitoring | Transformer inspection
2024-02-06 | 545 TR 1 | Maintenance routine | Transformer inspection
2024-02-06 | 552 TR 1 | Monitoring | Transformer inspection
2024-02-06 | 54A BM 1 | Troubleshoot | Disconnect cable supply for heating and bring to work shop
2024-02-06 | 535 BC 1 | Motor abnormal sound | Monitor bearing motor condition
2024-02-07 | 552 RP 1 | Maintenance routine (CNY 2024 stoppage) | Check carbon brush & slip ring contition ok. Check spring tension, carbon brush loosenes ok
2024-02-07 | 552 RP 2 | Maintenance routine (CNY 2024 stoppage) | Check carbon brush and slip ring contition ok. Check spring tension, carbon brush loosenes ok
2024-02-08 | 552 PP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-08 | 545 BM 1 | Isolate supply | Rack out GCB/VCB
2024-02-08 | 545 FN 16 | Isolate supply | Rack out GCB/VCB
2024-02-08 | 552 RP 1 | Isolate supply | Rack out GCB/VCB
2024-02-08 | 552 RP 2 | Isolate supply | Rack out GCB/VCB
2024-02-08 | 545 FN 14 | Isolate supply | Open ACB. Rack out.
2024-02-08 | 555 CP 3 | Isolate supply | Open ACB. Rack out.
2024-02-08 | 542 BE 1 M01 | Isolate supply | Off MCCB
2024-02-08 | 552 BE M01 | Isolate supply | Off MCCB
2024-02-08 | 552 BE 2 M01 | Isolate supply | Off MCCB
2024-02-08 | 540 BC 1 M01 | Isolate supply | Off MCCB
2024-02-08 | 540 BC 2 M01 | Isolate supply | Off MCCB
2024-02-08 | 552 BE 1 M02 | Isolate supply | Off MCCB
2024-02-08 | 552 BE 2 M02 | Isolate supply | Off MCCB
2024-02-08 | 545 SR 1 | Isolate supply | Off MCCB
2024-02-08 | 545 SR 3 | Isolate supply | Off MCCB
2024-02-08 | 545 FN 15 | Isolate supply | Off MCCB
2024-02-08 | 545 SR 3 | Disconnect cable motor. | Work done
2024-02-08 | 545 FN 7 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 552 FN 7 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 545 FN 6 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 545 FN 8 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 550 BF 3 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 545 BF 2 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 542 BC 4 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 520 BC 8 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 545 FN 7 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 552 FN 7 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 545 FN 6 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 550 BF 3 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 545 BF 2 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 542 BC 4 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 520 BC 8 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 552 LQ 1 | Maintenance routine (CNY 2024 stoppage) | Dismantle , service and install motor. Bearing No: LS: 6205ZZ, WO: EE 778
2024-02-08 | 552 LQ 1 | Maintenance routine (CNY 2024 stoppage) | Dismantle , service and install motor. Bearing No: OLS: 6204ZZ
2024-02-08 | 552 LQ 2 | Maintenance routine (CNY 2024 stoppage) | Dismantle , service and install motor. Bearing No: LS: 6305ZZ WO: EE 779
2024-02-08 | 552 LQ 2 | Maintenance routine (CNY 2024 stoppage) | Dismantle , service and install motor. Bearing No: OLS: 6204ZZ
2024-02-08 | 545 FN 1 | Maintenance routine (CNY 2024 stoppage) | Dismantle , service and install motor. Bearing No: LS: 6308ZZ WO: EE774
2024-02-08 | 545 FN 1 | Maintenance routine (CNY 2024 stoppage) | Dismantle , service and install motor. Bearing No: OLS: 6208ZZ
2024-02-08 | 545 FN 7 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6308
2024-02-08 | 545 FN 7 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6208
2024-02-08 | 552 FN 7 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6308
2024-02-08 | 552 FN 7 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6306
2024-02-08 | 545 FN 6 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6308
2024-02-08 | 545 FN 6 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6208
2024-02-08 | 545 FN 8 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6308
2024-02-08 | 545 FN 8 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6208
2024-02-08 | 550 BF 3 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6208
2024-02-08 | 550 BF 3 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6205
2024-02-08 | 545 BF 2 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6207
2024-02-08 | 545 BF 2 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6206
2024-02-08 | 542 BC 4 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6307
2024-02-08 | 542 BC 4 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6206
2024-02-08 | 520 BC 8 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6206
2024-02-08 | 520 BC 8 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6205
2024-02-08 | 545 FN 10 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6308
2024-02-08 | 545 FN 10 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6208
2024-02-09 | 561 CP 2 | Alarm overload at CCR | Check at CP alarm. Service DP air filter
2024-02-09 | 542 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-09 | 542 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-09 | 562 AD 1 M01 | Alarm A25 | Isolate & normalize supply
2024-02-09 | Blow tank CM3 | Service request: Exhaust valve | Disconnect cable (220V)
2024-02-09 | 552 BE 2 M02 | Normalize fuse form | On MCCB
2024-02-09 | 552 CP 1 | Isolate supply | Off MCCB (Isolator)
2024-02-09 | 552 CP 2 | Isolate supply | Off MCCB (Isolator)
2024-02-09 | 540 WP 2 | Isolate supply | Off overload breaker
2024-02-09 | 542 BC 4 | Isolate supply | Off MCCB
2024-02-09 | 555 CP 3 | Isolate supply | Off MCCB
2024-02-09 | 535 BC 1 | Isolate supply | Off MCCB. Work done
2024-02-09 | 540 BC 1 | Normalize supply | On MCCB
2024-02-09 | 545 FN 7 | Maintenance routine (CNY 2024 stoppage) | Motor LV Maintenance - Service motor. Install motor at site. WO EE 765
2024-02-09 | 552 FN 7 | Motor LV Maintenance - Service motor. Install motor at site. WO EE 776 | Cement Mill & Packing CNY 2024 stoppage
2024-02-09 | 545 FN 6 | Maintenance routine (CNY 2024 stoppage) | Motor LV Maintenance - Service motor. Install motor at site. WO EE 766
2024-02-09 | 550 BF 3 | Motor LV Maintenance - Service motor. Install motor at site. WO EE 777 | Cement Mill & Packing CNY 2024 stoppage
2024-02-09 | 545 BF 2 | Maintenance routine (CNY 2024 stoppage) | Motor LV Maintenance - Service motor. Install motor at site. WO EE 769
2024-02-09 | 545 FN 13 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor and service .WO : EE 765
2024-02-09 | 545 FN 8 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor and service .WO : EE 767
2024-02-09 | 545 FN 10 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor and service .WO : EE 773
2024-02-09 | 542 BC 4 | Maintenance routine (CNY 2024 stoppage) | ContInue service motor WO : EE 770/ oil seal
2024-02-09 | 520 BC 5 | Maintenance routine (CNY 2024 stoppage) | ContInue service motor WO : EE 772
2024-02-09 | 545 FN 7 | Installation | Install and dismantle motor CM3 - complete
2024-02-09 | 552 FN 7 | Installation | Install and dismantle motor CM3 - complete
2024-02-09 | 545 FN 6 | Installation | Install and dismantle motor CM3 - complete
2024-02-09 | 550 BF 3 | Installation | Install and dismantle motor CM3 - complete
2024-02-09 | 545 BF 2 | Installation | Install and dismantle motor CM3 - complete
2024-02-09 | 545 FN 10 | Installation | Install and dismantle motor CM3 - Ready to install. After completing the service do an insulation test
2024-02-09 | 520 BC 8 | Installation | Install and dismantle motor CM3 - Ready to install. After completing the service do an insulation test
2024-02-09 | 542 BC 4 | Installation | Install and dismantle motor CM3 - Ready to install. After completing the service do an insulation test
2024-02-09 | 545 FN 13 | Installation | Install and dismantle motor CM3 - Ready to install. After completing the service do an insulation test
2024-02-09 | 545 FN 8 | Installation | Install and dismantle motor CM3 - Ready to install. After completing the service do an insulation test
2024-02-10 | 552 BE M02 | Normalize supply | On MCCB
2024-02-10 | 552 BE M01 | Normalize fuse form | On MCCB
2024-02-10 | 552 BE M01 | Normalize fuse form | On MCCB
2024-02-10 | 535 VV 4 | New Installation (gate) | Install sensor close/open. Test signal open/close. Replace valve.Test local cannot operate. By pass piping still cannot open. Suspect gate stuck. Follow up needed. 19.7.2. Open. 19.7.3.Close. Command: 22.3.4
2024-02-10 | 545 FN 15 | Service request: Isolate supply | Isolate & normalize supply
2024-02-10 | 561 RL 1 M03 | Isolate supply | Off MCCB. Work done
2024-02-10 | 560 BC 1 | Isolate supply | Off MCCB. Work done
2024-02-10 | 561 BC 3 | Isolate supply | Off MCCB. Work done
2024-02-10 | 561 BC 4 | Isolate supply | Off MCCB. Work done
2024-02-10 | 545 FN 10 | Installation | Install motor CM3
2024-02-10 | 520 BC 8 | Installation | Install motor CM4
2024-02-10 | 542 BC 4 | Installation | Install motor CM5
2024-02-10 | 545 FN 8 | Installation | Install motor CM3
2024-02-10 | 545 FN 15 | Installation | Install motor CM3
2024-02-10 | 54A BM 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 55A TR 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 54B BM 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 55B TR 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 545 TR 1 | Maintenance routine | Cleaning TX room and TX
2024-02-10 | 552 TR 1 | Maintenance routine | Cleaning TX room and TX
2024-02-10 | 545 FN 16 | Installation | Install motor at site
2024-02-10 | 545 FN 8 | Installation | Install motor at site
2024-02-10 | 545 FN 10 | Installation | Install motor at site
2024-02-10 | 542 BC 4 | Installation | Install motor at site
2024-02-10 | 520 BC 8 | Installation | Install motor at site
2024-02-10 | 545 TR 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 552 TR 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 54A BM 1 01 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 560 TR 1/CM4 DEPT | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 545 BM 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 54B TR 1/DEPT | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 54B BM 1 01 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 54B TR 1/DEPT | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | CM3 | Hoist not function | Check found supply. Genset not running. Genset problem 2x stop. Follow up needed.
2024-02-10 | 510 BE 1 | Isolate supply | Work done
2024-02-10 | 510 BE 2 | Isolate supply | Work done
2024-02-10 | 535 AC 1 | Isolate supply | Work done
2024-02-10 | 545 SR 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-10 | 545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-10 | 555 CP 3 | Normalize fuse form | On MCCB
2024-02-10 | 542 BE 2 | Normalize fuse form | On MCCB
2024-02-10 | 535 BC 1 | Normalize fuse form | On MCCB
2024-02-10 | 510 BE 2 | Normalize fuse form | On MCCB
2024-02-10 | 510 BE 1 | Normalize fuse form | On MCCB
2024-02-10 | 561 RL 1 | Service request: Isolate supply | VCB cannot work-out. Power cut off control breaker. Rack-out after power cut.
2024-02-10 | 545 SC 1 | Cover fan out position / motor no cooling fan | Install fan take from workshop and fix back cover fan.
2024-02-10 | 552 RP 1 | Check siren start warning | Check out put, relay output and supply 220V. Follow up needed.
2024-02-10 | 552 RP 2 | Check siren start warning | Check out put, relay output and supply 220V. Follow up needed.
2024-02-10 | 545 BM 1 | Check siren start warning | Check output, relay output and supply 220V. Follow up needed.
2024-02-11 | 545 FN 16 01 | Maintenance routine | WO: EE718. Motor and starter maintenance. Blow motor, slip ring and filter. IR test starter . R-E: 5 KV. Y-E: 5KV. B-E: 5KV. Lift up resistance starter and check all contact and resistor. Dismantle all fixed and moving contact bring back to workshop. Repair and service all the contact piece. Reinstall to starter, cleaning and renew oil.
2024-02-11 | 545 FN 16 01 | Maintenance routine | WO: EE718. Motor and starter maintenance. Blow motor, slip ring and filter. IR test rotor . R-E: 1 KV. Y-E: 1 KV. B-E: 1 KV. Lift up resistance starter and check all contact and resistor. Dismantle all fixed and moving contact bring back to workshop. Repair and service all the contact piece. Reinstall back to starter, cleaning and renew oil.
2024-02-11 | 545 FN 16 | Maintenance routine | Maintenance motor 545 FN 16 and starter. Insulation test starter 5 KV - 30 ohm - 3 minutes. Insulation test rotor 1 KV- Infinity 3 minutes. Replace oil starter 350 liter. Replace moving contact 6 pcs for start point and flatten the damaged all contact.
2024-02-11 | CM3 | Siren Mill. Siren roller press | Replace new siren. Siren roller press test.
2024-02-12 | 535 BC 9 | Normalize supply | On MCCB
2024-02-12 | 561 BC 4 | Normalize supply | On MCCB
2024-02-12 | 561 BC 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | 561 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | 560 BC 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | 561 BC 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | 561 RL 1 M03 | Normalize fuse form | On MCCB
2024-02-12 | 561 BC 4 | Normalize fuse form | On MCCB
2024-02-12 | 560 BC 1 | Normalize fuse form | On MCCB
2024-02-12 | 561 BC 3 | Normalize fuse form | On MCCB
2024-02-12 | 545 FN 15 | Normalize fuse form | On MCCB
2024-02-12 | CM3 (Siren) | Not function | Check and troubleshoot. Supply okay. 220V. (Relay WN9 Siren). Relay WN 10 lamp. Replace new siren. Test. Siren: 13.6.1. Lamp:13.6.2.
2024-02-12 | 561 RL 1 | Normalize supply | On MCCB
2024-02-12 | CM3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | CM3 | Lay cable for main drive CM3 - damaged | Prepare for cable pointer. Follow up needed.
2024-02-12 | 535 BC 9 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | 561 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | 535 AC 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 545 BE 1 | Isolate supply | Isolate & normalize supply
2024-02-13 | 540 BC 1 | Isolate supply | Isolate & normalize supply
2024-02-13 | 540 BC 2 | Isolate supply | Isolate & normalize supply
2024-02-13 | 542 BC 1 | Isolate supply | Isolate & normalize supply
2024-02-13 | 55B ITI Dept | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | CM3 (Exhaust valve blow tank) | A site: Cable snap | B site: Rejoint cable
2024-02-13 | 555 CP3 | Service request: Isolate supply | Rack in ACB
2024-02-13 | 510 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 510 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 542 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 542 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 562 AD 01 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 552 CP 3 | Not working | Check coil valve load unload
2024-02-13 | 545 BM1 | Cable punctured | Cut and reroute main drive cable. Training job have been carry on by cable jointer. Uncouple motor and test rotation. Amp per phase at power meter.
2024-02-13 | 545 FN 16 | Cable punctured | Cut and reroute cable. Jointing job have been carry on by cable jointer (Semmy). Cable size 16mm 3C XLPE
2024-02-13 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 545 SR 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 545 BM1 01 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 542 BC 4 | Overload 4x | Isolate & normalize supply
2024-02-13 | 545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 561 RL 01 | Isolate supply | Isolate & normalize supply
2024-02-13 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 545 SR 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 545 BM1 01 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 542 BC 4 | Overload 4x | Isolate & normalize supply
2024-02-13 | 545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 561 RL 01 | Isolate supply | Isolate & normalize supply
2024-02-13 | 510 BC 1 | Motion | Adjust speed switch. Test.
2024-02-13 | 540 BC 2 | Motion | Adjust speed switch. Test.
2024-02-13 | 545 FN 15 | Motor Testing | Test rotation for motor
2024-02-13 | 545 FN 10 | Motor Testing | Test rotation for motor
2024-02-13 | 545 FN 16 | Motor Testing | Test run control for starter position
2024-02-13 | 545 BM 1 | Cable punctured | Uncouple motor and test rotation. Amp per phase of power meter. L1: 11A, L2: 1A, L3: 12A. Low per phase at power meter, L1:17KW, L2:10KW, L3:18KW.
2024-02-13 | 545 FN 16 | Cable punctured | Cut and reroute cable. Joining job have been calling on by cable jointer. Cable saiz 16mm 3C XCPE.
2024-02-13 | 545 FN 15 | Cable at terminal MCC burn | Cut & rejoint
2024-02-13 | 545 FN 16 | Insulation test | Insulation test cable, after jointer finish. Start local for test rotation
2024-02-14 | 552 RP 1 | HT Motor monitoring, monitor carbon brush, slip ring and starter condition | All motor are in good condition.
2024-02-14 | 552 RP 2 | HT Motor monitoring, monitor carbon brush, slip ring and starter condition | All motor are in good condition.
2024-02-14 | 545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-14 | 545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-14 | 552 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-14 | 555 DY 1 | Alarm A01 -HP. Alarm A09 - Compressor overload. | Blow panel. Service aux contact service pressure switch. Reset pressure switch. Alarm clear. Test.
2024-02-15 | 510 AC 1 | maintenance routine | Greasing motor
2024-02-15 | 552 RP 1 | maintenance routine | Greasing motor
2024-02-15 | 552 RP 2 | maintenance routine | Greasing motor
2024-02-15 | 545 FN 12 | maintenance routine | Greasing motor
2024-02-15 | 545 FN 4 | maintenance routine | Greasing motor
2024-02-15 | 552 PP 1 | maintenance routine | Greasing motor
2024-02-15 | 550 FN 1 | maintenance routine | Greasing motor
2024-02-15 | 545 FN 14 | maintenance routine | Greasing motor
2024-02-15 | 545 FN 16 | maintenance routine | Greasing motor
2024-02-15 | 545 SR 3 | maintenance routine | Greasing motor
2024-02-15 | 545 SR 1 | maintenance routine | Greasing motor
2024-02-15 | 535 BC 4 | maintenance routine | Greasing motor
2024-02-15 | 552 FN 1 | maintenance routine | Greasing motor
2024-02-15 | 552 FN 2 | maintenance routine | Greasing motor
2024-02-15 | 552 PG 2 | Service request: check gate open 30% only at CCR | Check at site gate open 60%. Found part looser. Tighten back. Test.
2024-02-15 | 535 BC 5 | Alarm not ready | Isolate & normalize supply
2024-02-16 | 562 CP 1 | Isolate supply | Done
2024-02-16 | 562 CP 2 | Isolate supply | Done
2024-02-16 | 562 CP 3 | Isolate supply | Done
2024-02-16 | 532 CP 3 | Isolate supply | Done
2024-02-16 | 5632 AD 1 | Trip breaker overload | Check found compressor problem. Coil unbalance RB 3.2 BY 19.2 RY 19.2 Ohm
2024-02-16 | 552 RP 1 | Calibration | Calibrate gap sensor
2024-02-16 | 552 RP1 ZZ1Z01 | Calibration | Calibrate Gap sensor position left/Right
2024-02-16 | 552 RP1 ZZ1Z02 | Calibration | Calibrate Gap sensor position left/Right
2024-02-16 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-16 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-16 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-16 | 545 FN 4 | Service request: Isolate supply | Rack ACB & close
2024-02-16 | 545 FN 1 | Reading not showing at CCR | Check alarm. AL60 AD fail. Reset.
2024-02-17 | 562 AD 01 Drayer Cement Mill 4 | Alarm A09 | Check and found overload breaker trip. Reset.
2024-02-18 | 562 AD 01 Drayer Cement Mill 4 | Trip alarm A09 | Reset overload breaker.
2024-02-19 | 552 RP 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-19 | 552 RP 2 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-19 | 545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-19 | 545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-19 | 561 FN 2 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-19 | 561 RL 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-19 | 545 FN 15 | Monitoring | Cleaning motor body for bearing replacement. Follow up needed.
2024-02-19 | 555 AL 1 | CM3 (Blow tank B cannot discharge) | Service and adjust breaket limit switch receiver (A). Test run.
2024-02-19 | 552 CP 1 | Safety interlock | Isolate & normalize supply
2024-02-19 | 545 BC 1 | Overload | Isolate & normalize supply
2024-02-19 | 552 RP 1 | Machine fault | Reset starter.
2024-02-20 | 552 LQ 3 | Service request: to check alarm level SW | Check grease at tank. Try start manual. No alarm. Check pressure switch & test. Found pressure switch & test.
2024-02-20 | 542 BC 4 | Overload | Isolate & normalize supply
2024-02-20 | 545 FN 15 | Winding motor full of grease | Cleaning
2024-02-20 | 552 LQ 3 | Alarm level low | Check found pressure switch problem. Taken record pressure switch at Mechanical workshop. Test.
2024-02-21 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-21 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-21 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-21 | 542 BE 1 | maintenance routine | Greasing the following motor
2024-02-21 | 542 BE 2 | maintenance routine | Greasing the following motor
2024-02-21 | 552 BE 1 | maintenance routine | Greasing the following motor
2024-02-21 | 552 BE 2 | maintenance routine | Greasing the following motor
2024-02-21 | 555 CP 3 | maintenance routine | Greasing the following motor
2024-02-21 | 552 CP 1 | maintenance routine | Greasing the following motor
2024-02-21 | 552 CP 2 | maintenance routine | Greasing the following motor
2024-02-21 | 562 CP 3 | maintenance routine | Greasing the following motor
2024-02-21 | 561 CP 1 | maintenance routine | Greasing the following motor
2024-02-21 | 561 CP 2 | maintenance routine | Greasing the following motor
2024-02-21 | 562 CP 1 | maintenance routine | Greasing the following motor
2024-02-21 | 562 CP 2 | maintenance routine | Greasing the following motor
2024-02-21 | 562 CP 3 | maintenance routine | Greasing the following motor
2024-02-21 | 561 FN 2 | maintenance routine | Monitor carbon brush and slip ring. Top up 12 liter distill water for starter
2024-02-21 | 561 RL 1 | maintenance routine | Monitor carbon brush and slip ring. Top up 12 liter distill water for starter
2024-02-21 | 562 AD 1 | Check alarm 23:Temp. Low | Isolate & normalize supply
2024-02-21 | 562 CP 1 | Service request: Isolate supply | ON MCCB
2024-02-21 | 562 CP 2 | Service request: Isolate supply | ON MCCB
2024-02-21 | 562 CP 3 | Service request: Isolate supply | ON MCCB
2024-02-21 | 562 AD 01 | Alarm A23. Temp Low | EE Azim request adjust by pass hot gas valve (VB).Temp showing. 0.7 C - 5 C. Still monitor. Inform to EE Azim.
2024-02-22 | 54A LP 1 | Motor Testing | Test motor at workshop after bearing replacement. R-1.6, Y-1.7, B-1.7 .Install at site. Need to test rotation
2024-02-23 | 535 BC 7 | Insulation test | R-150. Y-150 B-151
2024-02-23 | 54A AS 1 | Motor Testing | Test local run - condition ok.
2024-02-23 | 54A AS 2 | Motor Testing | Test local run - condition ok.
2024-02-23 | 54A DA 1 | Motor Testing | Test local run - condition ok.
2024-02-23 | 54A WP 2 | Insulation test | R-200. Y-200 B-201
2024-02-23 | 54A WF 1 | Insulation test | R-250. Y-250 B-250
2024-02-23 | 54A WF 2 | Insulation test | R-250. Y-250 B-250
2024-02-23 | 54A WF 3 | Insulation test | R-200. Y-200 B-201
2024-02-26 | 552 RP 1 | Monitoring | HT Motor monitoring , Monitor carbon brush. Slip ring and starter condition
2024-02-26 | 552 RP 2 | Monitoring | HT Motor monitoring , Monitor carbon brush. Slip ring and starter condition
2024-02-26 | 545 FN 16 | Monitoring | HT Motor monitoring , Monitor carbon brush. Slip ring and starter condition
2024-02-26 | 545 BM 1 | Monitoring | HT Motor monitoring , Monitor carbon brush. Slip ring and starter condition
2024-02-26 | 561 FN 2 | Monitoring | HT Motor monitoring , Monitor carbon brush. Slip ring and starter condition
2024-02-26 | 561 RL 1 | Monitoring | HT Motor monitoring , Monitor carbon brush. Slip ring and starter condition
2024-02-26 | 54A WP 1 | Test local motor not run
2024-02-26 | 54A WP 2 | Uncouple motor found impeller full of rust | Uncouple motor found impeller full of rust. Clean impeller and fit back. Motor bearing ok. Test run ok.
2024-02-27 | 54A BM 1 | Starter problem | Check condition starter. Test manual ok. Lift up rheostart & check condition. Follow up needed.
2024-02-27 | 561 CP 1 | Compressor breakdown | Find cable for rental compressor 120mm3. Follow up needed.
2024-02-27 | 561 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-28 | 561 CP 2 | Cable not available | Lay temporary cable for rental compressor. 1 core 95 mm3 aluminium x 7 x 30 m connect at MCC and compressor. Follow up for testing.
2024-02-28 | 561 FN 2 | Troubleshoot | B05 1 01 - bearing temperature UAE. Replace transmitting. Test.
2024-02-28 | 552 RP 1 | maintenance routine | O&k Cement Mill 3 - Motor and starter maintenance
2024-02-28 | 552 RP 2 | maintenance routine | O&k Cement Mill 3 - Motor and starter maintenance
2024-02-28 | 545 FN 16 | maintenance routine | O&K CM3 - Motor and starter maintenance
2024-02-28 | 545 BM 1 | maintenance routine | O&K CM3 - Motor and starter maintenance
2024-02-28 | 590 VF 1 | Connect cable motor | Work together with normal group. Replace overload. Test.
2024-02-28 | 552 RP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-28 | 535 BC 5 | Not ready | Isolate & normalize supply
2024-02-29 | 561 CP 2 | Compressor testing | Rental compressor. Commissioning rental compressor. Unload - 150 A (R,Y,B). Load 230 A (R,Y,B)
2024-03-01 | 560 FN 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-01 | 561 CP 2 | Compressor installation | CNB 3:9:3.
2024-03-02 | 562 AD 1 | Alarm A23 | Isolate & normalize supply
2024-03-04 | 552 RP 1 | Monitoring | HT motor monitoring. Monitor carbon bruch, slip ring and starter condition for the following motor.
2024-03-04 | 552 RP 2 | Monitoring | HT motor monitoring. Monitor carbon bruch, slip ring and starter condition for the following motor.
2024-03-04 | 545 FN 16 | Monitoring | HT motor monitoring. Monitor carbon bruch, slip ring and starter condition for the following motor.
2024-03-04 | 545 BM 1 | Monitoring | HT motor monitoring. Monitor carbon bruch, slip ring and starter condition for the following motor.
2024-03-04 | 561 FN 2 | Monitoring | HT motor monitoring. Monitor carbon bruch, slip ring and starter condition for the following motor.
2024-03-04 | 561 RL 1 | Monitoring | HT motor monitoring. Monitor carbon bruch, slip ring and starter condition for the following motor.
2024-03-04 | 54A BM 1 | Troubleshoot | Starter. Connect back control cable and rotor cable. Check star point contactor. Ready for testing
2024-03-04 | 552 Bil (LC1) | Service request: Isolate supply | Isolate & normalize supply
2024-03-04 | 552 Bil (LC1) | Loose fuse | Tighten fuse
2024-03-04 | 555 VV 01 | Overload | Isolate & normalize supply
2024-03-04 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-04 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-04 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-04 | 552 RP 1 M01 | Trip alarm machine fault | Check and found. 552 LQ1 temp fluctuate. Check found cable loose. Cut and rejoint cable. Test.
2024-03-04 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-04 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-04 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-05 | 545 BM 1 | Insulation test | Test for spare motor. Starter 6.6 kv - 0 ohm. 1000v - 15 m ohm
2024-03-05 | CM3 | Replace 1 pc LED sportlight. 100 watt | Replace 1 pc LED sportlight. 100 watt
2024-03-05 | 520 BC 1 | Overload | Isolate & normalize supply
2024-03-06 | 54A BM 1 | Test switchgear spring tension snap during test | Check and repeat another one testing. Send to PL1 reading for starter testing.
2024-03-06 | 54A HP1 M01 P03 | service request: Oil supply pressure | check oil supply pressure.
2024-03-06 | 54A LP1 M01 P03 | Low pressure no reading (short circuit) | Check and cable damage. Replace new cable.
2024-03-06 | 545 FM 1 | Return flow meter not showing reading at CCR | Isolate & normalize supply
2024-03-06 | 545 FN 4 | Alarm vibration 545 FN4 VD1. V41 | Reset failed. Follow up needed.
2024-03-07 | 545 FN4 - VD1-V41 | Alarm vibration | Found bolt base sensor damaged. Tighten back. Reset at panel nearby motor. Start syatem.
2024-03-07 | 54A BM 1 | Motor Testing | Test control motor. Starter up and down position ok. Start point contactor ok. Switch gear open and close. Work complete for test.
2024-03-07 | 565 CP 3 | maintenance routine | Check at compressor alarm oil temperature and service. Follow up needed.
2024-03-08 | 545 BM 1 | Mill stop but GCB 13 still in close position | Manually open GCB at ER PPD. Bring back to workshop and service. Follow up needed.
2024-03-08 | 545 BM 1 | Mill cannot stop | Try manual stop. Bring GCB to workshop for check and repair. GCB cannot open and close. Mechanical problem. To find another GCB for check and repair. Replace 1 closing coil (733 ohm). Replace 1 tripping coil (43.6 ohm). Replace 2 stopper. Test open/close 3x. Rack in and handover to production. Need to repair 1 unit for spare.
2024-03-09 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 561 RL 1 M03 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 561 RL1 M03 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-10 | 561 DL 1 | Check carbon brush and starter. trequest ny EE Azim. | All in good condition
2024-03-11 | 545 BM 1 | Switchgear | Try to repair and service but still cannot solve problem. Follow up needed.
2024-03-11 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-11 | 545 FM 1 | Flow meter not showing reading at CCR | Alarm at panel. Reset
2024-03-12 | 552 RP 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-12 | 552 RP 2 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-12 | 545 FN 16 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-12 | 545 BM 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-13 | 54A CP 1 M01 P02 | Pressure abnormal reading | Replace transmitter pressure but reading still show not normal. Follow up needed.
2024-03-14 | 545 TR 01 | Maintenance routine | Transformers inspection
2024-03-14 | 552 TR 01 | Maintenance routine | Transformers inspection
2024-03-14 | 54A TR 01 | Maintenance routine | Transformers inspection
2024-03-14 | 55B TR 01 | Maintenance routine | Transformers inspection
2024-03-14 | 561 TR 01 | Maintenance routine | Transformers inspection
2024-03-15 | 560 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-15 | 555 VV1 01 | Both limit | Server limit switch. Test.
2024-03-15 | 561 FN 2 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-15 | 561 RL 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-15 | 562 CP 01 | maintenance routine | Greasing motor
2024-03-15 | 562 CP 02 | maintenance routine | Greasing motor
2024-03-15 | 562 CP 03 | maintenance routine | Greasing motor
2024-03-15 | 561 RL 1 M03 | maintenance routine | Greasing motor
2024-03-15 | 561 FN 1 | maintenance routine | Greasing motor
2024-03-15 | 561 RL 1 | maintenance routine | Greasing motor
2024-03-15 | 561 FN 2 | maintenance routine | Greasing motor
2024-03-15 | 560 FN 1 | maintenance routine | Greasing motor
2024-03-16 | 561 RL01 M01 P03 | Roller No.3. Alarm at panel (Burn out) | Isolate & normalize supply
2024-03-16 | 555 VV01 | Both limit on | Gate stuck. Service limit. Test.
2024-03-16 | 561 AL 01 | Service request: Isolate supply | Isolate & normalize supply
2024-03-18 | 561 FN 16 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 552 RP 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 552 RP 2 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 545 BM 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 561 FN 2 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 561 RL 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 545 FN 16 | pcs routine | Replace carbon brush 3 pcs
2024-03-18 | 561 RL 1 | Water level starter low | Topup water 12 liter
2024-03-18 | 545 BM 1 | Service GCB for 545 BM 1 but still not working | follow up needed
2024-03-18 | 552 CP 3 | Alarm starter feedback contact | Isolate & normalize supply
2024-03-18 | 510 AC 1 | Overload | Isolate & normalize supply
2024-03-18 | 561 FN 16 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 552 RP 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 552 RP 2 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 545 BM 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 561 FN 2 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 561 RL 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 555 VV 1 | Alarm runtime | Isolate & normalize supply
2024-03-20 | 542 BC 4 | Overload | Isolate & normalize supply
2024-03-20 | 552 BE 1 M01 L44 | Alarm high-high | Wire loose. Tighten wire.
2024-03-20 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-20 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-20 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 561 FN 2 | Water level starter low | Topup water 12 liter. Continue checking switchgear at workshop but still not ok. Follow up needed.
2024-03-21 | 561 RL 1 | Isolate supply | Rack out VCB
2024-03-21 | 561 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 540 WF 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 540 SX 2 | Overload (3x)y. 0.75 kw. 4 pole. | Reset, Clamp Amp R-1.8A, Y-0A, B-1.8A. Check found 1 phase coil open. replace motor. Test. clamp Amp. R-1.2A, Y-1.2A, B-1.2A.
2024-03-21 | 561 RL 1 | Service request: Isolate supply | Rack in VCB
2024-03-21 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-22 | 561 CLA1 | Check pump grease request by attendant | Check and setting timer.Test ok. Done work together with Mechanical team.
2024-03-22 | 545 SR3 P01 | Classifier inlet pressure reading fluctuate | Disconnect cable try. Continuty test. Found signal cable to AI no continuity suspect snap. Replace spare cable. (AI-22:6:6)
2024-03-23 | 535 BC 5 | Overload | Isolate & normalize supply
2024-03-23 | 555 CP 3 | Alarm overload at CCR | Check at CP alarm overload fan motor, Reset. Alarm service and alarm DP oil filter. Inform production and mechanical to continue check.
2024-03-24 | 555 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-24 | 542 MS 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-24 | 542 BC 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-24 | 555 CP 3 | Rental Comp -Cable incoming snap | Cut for 'vendor' to check compressor for futher action. Cable incoming has not been installed yet.
2024-03-24 | 552 BF 2 | Miller request to check not purging | Try local check supply. Check and troubleshoot found cable snap at card. Connector problem. Replace connector. Test local.
2024-03-24 | 542 BC 2 | Service request: Isolate supply | On MCCB
2024-03-24 | 542 MS 1 | Service request: run control | Loop terminal 1, 2, 3 for ready
2024-03-24 | 535 BC 5 | Not ready cover load | Isolate & normalize supply
2024-03-25 | 552 BE M01 L44 | Alarm RP outlet chute level high | Service and clean level sensor. Done
2024-03-25 | 552 RP 1 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition
2024-03-25 | 552 RP 2 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition
2024-03-25 | 545 FN 16 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition
2024-03-25 | 545 BM 1 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition
2024-03-25 | 561 BM 1 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition
2024-03-25 | 561 FN 2 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition
2024-03-26 | 54A BM 1 | Troubleshoot | Replace socket 5 pin to 4 pin. lay cable for booster 30kw. Contactor service and cleaning 54 BM 1. Supervise contactor DC motor
2024-03-26 | 562 MW 1 | Overload | Isolate & normalize supply
2024-03-26 | 555 AL 1 LLPL41 (Hopper level) | Alarm level high | Check suspect sensor problem. Follow up needed.
2024-03-27 | 555 AL 1 | Continue from (Shift, Alarm hopper level high) | Replace level take form workshop.Test signal.
2024-03-27 | 562 MW 1 | Service request: Adjust gate | Adjust gate open. Close.
2024-03-27 | 552 CP 3 | Service request: Megger | Request megger motor
2024-03-27 | 542 MS 1 | Install panel. Connect cable supply and cable for DC. Waiting for cement mill stop for connect cable for site. Supervise contactor VC motor. | Install panel. Connect cable supply and cable for DC. Waiting for cement mill stop for connect cable for site. Supervise contactor VC motor.
2024-03-28 | 552 SG 3 | Alarm fault | Check found breaker. 48V trip. Reset.
2024-03-28 | 552 RF 1 | Service request: Alarm moveable roller left/high end | Check found 48V breaker trip. Try reset and start back still trip 48V breaker and same alarm hopper. Check sensor ok and gap at mimic 38 days and 40 days. Follow up needed.
2024-03-29 | 552 RP 1 | Troubleshoot | Reset start still trip. Continue check by normal group. Follow up needed.
2024-03-29 | 552 RP 1 | Troubleshoot | Check found 552 RP 2 TS 2 cable short (moveable roller temp no.high). Disconnect cable no: 57. Test.
2024-03-29 | 552 RP 1 | Troubleshoot | Continue check shift personal
2024-03-29 | 542 MS 1 | Troubleshoot | Connect cable & test.
2024-03-29 | 542 BC 2 | Troubleshoot | Connect cable & test.
2024-03-29 | 54A BM 1 | Monitoring | Supervise VC and hand over by VC Motor
2024-03-29 | 545 FM 2 | Alarm | Isolate & normalize supply
2024-03-30 | 552 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-30 | 562 MW 01 | Overload | Isolate & normalize supply
2024-03-30 | 562 MW 03 | Overload | Isolate & normalize supply
2024-03-30 | 562 MW 03 | Overload | Isolate & normalize supply
2024-03-31 | 562 MW 1 | Overload | Isolate & normalize supply
2024-03-31 | 562 MW 3 | Overload | Isolate & normalize supply
2024-03-31 | 561 CLA 1 | Overload | Check found cable snap. Repair &test.
2024-04-01 | 542 BF 2 | Not purging | Check no supply and card problem, have informed the normal group.
2024-04-01 | 552 RP 1 | Monitoring | HR Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-04-01 | 552 RP 2 | Monitoring | HR Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-04-01 | 545 FN 16 | Monitoring | HR Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-04-01 | 545 BM 9 | Monitoring | HR Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-04-01 | 561 RL 1 | Monitoring | HR Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-04-01 | 561 FN 2 | Monitoring | HR Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-04-01 | 561 RL 1 | Motor level starter show low | Topup water 12 liter at starter
2024-04-01 | 54A BM 1 | Insulation test | Test for Rotor-1kv - ohm. Stater- 5 kv-100m ohm. Cable- 5kv-800m ohm. Connect cable at GCB, compartment. Connect cable at terminat motor. On heater and add on extra heat rotor with spotlight.
2024-04-01 | 545 BF 02 | Troubleshoot | Check and rectify. Not purging. check and troubleshoot found card.
2024-04-01 | 542 BF 02 | Bag filter burnt | Bag filter, check and troubleshoot, found card burned 2 pcs.
2024-04-01 | 562 CP 3 | Main breaker trip. Megger motor shorted. | Dismantle motor.
2024-04-01 | 510 GA 3 | Overload | Isolate & normalize supply
2024-04-02 | 54A BM 1 | Insulation Test | Topup water for starter 84 liter. Add heater blower 2 pcs. Insulation test rotor. R-E - 1 KV -0.5 M Ohm. Y-E- 1 KV-0.5 M Ohm. B-E-1 KV - 0.5 M Ohm. Follow up needed.
2024-04-05 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-04-05 | 562 cp 2 | Service request: Isolate supply | Isolate & normalize supply
2024-04-05 | 545 BM 1 M07 | Trip MCCB | Cable nurn at terminal motor. Repair & test.
2024-04-06 | 545 BM1 M07 | Alarm not ready. * 18.5 kw, * 6 pole, * 35 A | Check MCCB Trip. Check found cable blue burn at terminal and touch yellow phase. Megger motor ok. Repair and replace terminal. Test ok. R-20.7A, Y-21.1A, B-20.7A.
2024-04-06 | 561 CL A1 | Service request: run manual pump grease | By pass timer and select on local switch pump run. Pump on 2 hour and motor run 2 minute.
2024-04-06 | 561 CLA 01 | Service request: Isolate supply | Isolate & normalize supply
2024-04-06 | 545 FM 2 | Alarm stop machine | Reset panel
2024-04-06 | 561 CLA 01 | Motor on the gearbox | Disconnect cable motor
2024-04-07 | 561 CLA 01 | Service request: Isolate supply | Isolate & normalize supply
2024-04-07 | 561 CLA 01 | Vibration cable | Connect cable vibration
2024-04-08 | 54 A BM 1 | Insulation test | Test for starter & motor.
2024-04-09 | 545 BM 1 M02 | Inching motor local switch problem | Check & service. Test.
2024-04-09 | 561 GR 01 | Overload | Isolate & normalize supply
2024-04-14 | 552 CP 03 | Assist shift | Rejoint cable & restart
2024-04-14 | 552 CP 3 | Alarm motor overload | Check found cable explode at terminal. Rejoint cable.
2024-04-15 | 561 CP 1 | Trip | Isolate & normalize supply
2024-04-15 | 545 FM 2 | Flow not show. Alarm AL60 AD fail | Isolate & normalize supply
2024-04-16 | 552 RP 1 | Starter fault | Starter not in position. Reset.
2024-04-16 | 561 RL 01 | Service request: Isolate supply | Isolate & normalize supply
2024-04-16 | 561 BC 01 | Overload | Isolate & normalize supply
2024-04-16 | 545 FM 2 | Flow not show. | Isolate & normalize supply
2024-04-17 | 545 FM 2 | Flow not show | Isolate & normalize supply
2024-04-18 | 561 RL 01 | Monitoring | HT Motor monitoring, monitor carbon brush slip ring & starter condition
2024-04-18 | 561 FN 02 | Monitoring | HT Motor monitoring, monitor carbon brush slip ring & starter condition
2024-04-18 | 545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush slip ring & starter condition
2024-04-18 | 552 RP 1 | Monitoring | HT Motor monitoring, monitor carbon brush slip ring & starter condition
2024-04-18 | 552 RP 2 | Monitoring | HT Motor monitoring, monitor carbon brush slip ring & starter condition
2024-04-18 | 545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush slip ring & starter condition
2024-04-19 | 545 FM 2 | Alarm AL/60 AD fail | Isolate & normalize supply
2024-04-20 | 545 SF 1 | Door panel bag filter | Can't install lock door panel because not suitable with old lock
2024-04-22 | 561 FN 2 | Topup water 12 liter at starter | Topup water 12 liter at starter. Replace carbon brush 18 pcs. (E-carbon) direct change. Blow slip ring and filter.
2024-04-22 | 552 BC 2 | Service request: Isolate supply | Isolate & normalize supply
2024-04-22 | 540 BC 1 | Service request: Isolate supply | Isolate & normalize supply
2024-04-23 | 562 CP 3 | New Installation | Install motor CP at Cement Mill 4. Connect cable and test rotation, but wrong rotation. Change cable connection and test again.
2024-04-23 | Group 535 | Not ready. 48V trip | Terminal cable 23,24 short (D/S). Check D/S 535 BL 5. Service, repair, & test.
2024-04-23 | 542 FN 3 | Service request: Isolate supply | Isolate & normalize supply
2024-04-23 | 580 PG 2 | Cannot open/close | Rejoint cable and restart
2024-04-23 | 552 RP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-04-24 | 535 BC 2 | Service request: Isolate supply | Isolate & normalize supply
2024-04-24 | 535 BC 2 | Service request: Isolate supply | On MCCB
2024-04-24 | 545 FM 1 | Alarm AL/60 AD fail. Reading not showing at CCR. | Isolate & normalize supply
2024-04-24 | 545 FN 16 | Alarm not ready. Fan stop run | Check VCB. No alarm. Check starter no alarm. Ready to start. Restart inform to miller, monitor for one half an hour. If the condition is normal, continue start feed.
2024-04-25 | 54A BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-04-25 | 54A BE 2 | Service request: Isolate supply | Isolate & normalize supply
2024-04-25 | 54B SC 2 | Overload | Isolate & normalize supply
2024-04-25 | 54A BE 1 | Service request: Isolate supply | On MCCB
2024-04-25 | 54A BE 2 | Service request: Isolate supply | On MCCB

## C.Mill 3 (visualize)
Date | Equipment # | Issues | Resolution | equipment | count
2023-08-28 | 562 MW | Overload | Isolate & normalize supply
2023-09-14 | 552 RP 1 | Service request: Isolate supply | Rack out VCB
2023-09-14 | 553 RP 1 | Service request: Isolate supply | Rack out VCB
2023-09-15 | 552 RP 2
2023-09-16 | 553 RP 2
2023-08-25 | 51A GA S | Overload | Isolate & normalize supply
2023-08-25 | 520 BC 1 | Alarm return fault | Isolate & normalize supply
2023-08-25 | 520 GA 1 | Shaft snap | follow up needed
2023-08-25 | 520 SG 1 | Overload | Isolate & normalize supply
2023-08-28 | 535 BC 5 | Overload | Isolate & normalize supply
2023-09-07 | 535 BC 6 | Overload | Isolate & normalize supply
2023-09-07 | 535 BC 9 | Overload | Isolate & normalize supply
2023-08-29 | 535 BC 5 | Overload | Isolate & normalize supply
2023-09-05 | 540 SX 2 | Overload | Isolate & normalize supply
2023-09-14 | 545 FN 4 | Rack in ACB | Close ACB
2023-09-14 | 545 FN 4 | Rack out ACB | Open ACB
2023-09-08 | 54B AC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-09-08 | 54B AC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-09-08 | 54B AC 1 | Service request: Disconnect cable speed switch | Disconnect cable speed switch. Reset.
2023-08-31 | 550 FN 1 | Overload | Isolate & normalize supply
2023-09-02 | 552 BC 1 | Overload | Isolate & normalize supply
2023-08-28 | 552 BL 1 | Overload | Isolate & normalize supply
2023-09-11 | 552 BL 1 | Overload | Check coil motor at MCC. Restart.
2023-09-12 | 552 BL 1 | Overload | Isolate & normalize supply
2023-09-12 | 552 BL 1 | Overload | Isolate & normalize supply
2023-09-14 | 552 BL 1 | Overload | Isolate & normalize supply
2023-09-01 | 552 HT 1 | WO CE 786 - abnomal sound | Check and replace motor.
2023-08-25 | 552 RP 1 | Machine fault - starter not in high position | Isolate & normalize supply
2023-08-28 | 552 RP 1 | Alarm starter rods not in high position | Isolate & normalize supply
2023-09-14 | 552 RP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-09-14 | 552 RP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-08-25 | 552 SG 3 | Attendance info base portion | Replace new base an restart. Follow up needed.
2023-09-02 | 552 SG 3 | Overload | Isolate & normalize supply
2023-09-08 | 552 SG 3 | Overload | Isolate & normalize supply
2023-09-08 | 552 SG 3 | Overload | Isolate & normalize supply
2023-09-12 | 552 SG 3 | Overload | Isolate & normalize supply
2023-09-13 | 552 SG 3 | Overload | Isolate & normalize supply
2023-09-14 | 552 SG 3 | Overload | Isolate & normalize supply
2023-08-29 | 555 BF 3 | Overload | Isolate & normalize supply
2023-08-28 | 555 DY 1 | alarm cannot reset at panel (A09) | Isolate & normalize supply
2023-09-10 | 560 BC 1 | Overload | Isolate & normalize supply
2023-09-05 | 560 BF 3 | Overload | Isolate & normalize supply
2023-09-06 | 560 BF 3 | Overload | Isolate & normalize supply
2023-09-13 | 561 FN 2 | Maintenance routine | Top up 12 liter distill water for starter.
2023-09-06 | 561 PG 1 | Cannot moving - WO (EC791) | Replace valve
2023-09-09 | 561 RL 1 | Low pressure | Repair key way problem
2023-09-09 | 561 RL 1 | Alarm starter not in first step | Isolate & normalize supply
2023-09-14 | 561 RL 1 | Alarm starter not in first step | Isolate & normalize supply
2023-09-11 | 561 RL 4 | Alarm return fault at CCR | Tighten control cable at contector and aux contact
2023-09-01 | 561 RL 1 | WO CE 787 - Temp. fluctuate | Replace PT 101
2023-09-09 | 562 AD 1 | Alarm A25 | Isolate & normalize supply
2023-08-29 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-09-02 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-09-10 | 562 CP 1 | Fan motor overload | Isolate & normalize supply
2023-08-29 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-09-02 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-08-29 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-09-02 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-08-28 | 562 FN 1 | Overload | Isolate & normalize supply
2023-09-02 | 562 HT 1 | Service request | Service motor
2023-08-28 | 562 MW 3 | Overload | Isolate & normalize supply
2023-08-28 | 562 MW 1 | Gate not fully open at site. CCR open. | Adjust limit switch
2023-08-28 | CM3 | Trip | Isolate & normalize supply
2023-09-10 | CM3 | CM3 & CM4 running smoothly | Standby
2023-09-11 | CM3 : 1. 545 FN 14, 2. 545 FN 15, 3. 545 FN 16, 4. 545 SR 3, 5. 545 SR 1 , 6. 535 BC 4, 7. 552 BE 1, 8. 552 BE 2, 9. 542 BE 1, 10. 542 BE 2, 11. 550 FN 1, 12. 552 FN 2 | Maintenance routine | Greasing motor
2023-08-25 | Fire alarm | Alarm | Isolate & normalize supply
2023-09-13 | 1. 555 CP 3, 2. 552 CP 1 3. 552 CP 2, 4. 510 AC 1, 5. 545 FN 4, 6. 552 FN 1 | Maintenance routine | Greasing Motor
2023-09-13 | Gypsum weighfeeder | Calibration | Gypsum weighfeeder physical calibration done
2023-09-16 | 54B AC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-09-18 | 552 BC 2 | Service request: Isolate supply | Isolate & normalize supply
2023-09-18 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2023-09-18 | 552 BC 2 | Service request: Isolate supply | Isolate & normalize supply
2023-09-18 | 550 RF 2 | Overload | Isolate & normalize supply
2023-09-18 | T5481 | Material to cement silo temp - open loop | follow up needed
2023-09-20 | 545 BM 1 | C shift drive cannot start bush lifting fault | Alarm at Panel control motor for RR faulire. Try force camcon to up position but reached on step machinism stuck. check and found the steering lock not in position. Try manual stary from CCR.
2023-09-20 | 552 BL 1 | Overload | Isolate & normalize supply
2023-09-21 | 548 AC 1 | Check speed switch and ropeswitch | Check and replace speed switch and ropeswitch
2023-09-21 | T5481 | WO CE802 - open loop | Replace terminator
2023-09-22 | 560 BP 3 | Overload | Isolate & normalize supply
2023-09-22 | 5340 BP 2 | WO RE239 Overload- 0.75 kW | Check motor 1 phase missing - normal group continue replace motor space.
2023-09-25 | 545 FN 4 | Rack out ACB | Isolate & normalize supply
2023-09-25 | 560 BF 1 | Overload | Isolate & normalize supply
2023-09-25 | 510 BF 1 | Overload | Isolate & normalize supply
2023-09-25 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2023-09-25 | 561 BC 3 | Overload | Isolate & normalize supply
2023-09-25 | 51A GA S | Copper tank damage, gear for limit switch problem | Calibrate close/open gate
2023-09-26 | 560 BF 3 | Cable snap | Rejoint. Start but still trip overload. Disconnect cable and dismantle motor.
2023-09-26 | 552 BL 1 | Overload | Isolate & normalize supply
2023-09-27 | 560 BF 3 | New Installation | Prepare motor
2023-09-27 | 560 BF 3 | New Installation | Replace motor
2023-09-27 | 561 BC 3 | Overload | Isolate & normalize supply
2023-09-28 | 560 BP 3 | New Installation | test free run without load clamp amp. R= 11.64 Y=11.54 B=11.64
2023-09-28 | 560 BF 3 | Contactor stuck | Service contactor
2023-09-28 | Drayer CM3 | Trip overload breaker (alarm A09) | Service aux contact. Restart
2023-09-29 | CM3 - Stack 7 | Service request: Tidy up cable analog | Tidy up cable analog
2023-09-30 | 535 BC 5 | Overload | Isolate & normalize supply
2023-10-01 | CM3 | Running smoothly | Standby
2023-10-01 | 561 RL 1 | Alarm starter first stop | Isolate & normalize supply
2023-10-02 | 561 RL 1 | High vibration DE and NDE motor | Replace 22 pcs c/brush due to short. S/C 184291. WO-129160.
2023-10-02 | 561 BC 3 | Overload | Isolate & normalize supply
2023-10-02 | 560 RF 1 | Control breaker trip | Return fault
2023-10-02 | 561 BC 3 | cable snap | Rejoint cable and restart
2023-10-02 | 570 FN 1 | Overload | Isolate & normalize supply
2023-10-02 | 561 RL 1 | NDE/DE vibration alarm | Replace IFM sensor
2023-10-02 | 570 FN 1 | Motor short | Disconnect cable motor. Follow up needed.
2023-10-04 | 535 BC 2 | Service request: Isolate supply | off MCCB
2023-10-04 | 535 BC 5 | Service request: Isolate supply | off MCCB
2023-10-04 | 535 BC 2 | Service request: Isolate supply | on MSSB
2023-10-04 | 535 BC 5 | Service request: Isolate supply | on MSSB
2023-10-04 | 545 FN 16 | Service request: Isolate supply | Rack out VCB
2023-10-04 | 552 RP 1 | Service request: Isolate supply | Rack out VCB
2023-10-04 | 552 RP 1 | Service request: Isolate supply | Rack out VCB
2023-10-04 | 540 BC 1 | Service request: Isolate supply | off MCCB
2023-10-04 | 540 BC 2 | Service request: Isolate supply | off MCCB
2023-10-04 | 510 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-04 | 510 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-04 | 552 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-04 | 552 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-04 | 552 RP 1 | Maintenance routine | Check carbon/brush, s/ring and starter
2023-10-04 | 552 RP 1 | Maintenance routine | Check carbon/brush, s/ring and starter
2023-10-04 | 545 FN 16 | Maintenance routine | Check carbon/brush, s/ring and starter
2023-10-04 | 552 BL 2 | Check and test motor free run. | Test free run
2023-10-04 | 510 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-04 | 510 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 545 BM 1 | Service request: Isolate supply | Rack out GCR
2023-10-05 | 545 FN 4 | Service request: Normalize fuse form | Normalize fuse form
2023-10-05 | 545 SR 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 561 BC 3 | Overload | Isolate & normalize supply
2023-10-05 | 565 CP 3 | Service request: Isolate supply | Rack out ACB
2023-10-05 | 542 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 540 BC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 535 BC 4 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 552 RP 1 | Service request: Isolate supply | Rack in VCB
2023-10-05 | 552 RP 2 | Service request: Isolate supply | Rack in VCB
2023-10-05 | 545 BM 1 | Maintenance routine | Check brush lifting compartment and starter
2023-10-05 | 520 GA 1 | Service request: check gate | Adjust limit switch
2023-10-05 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 545 FN 16 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 552 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 552 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 535 BC 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 535 BC 5 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | CM3 | cable snap | Rejoint cable and restart
2023-10-05 | 540 BC 2 | alarm motion | Check and found base speed. Switch loose. Adjust & tighten bolt & nut. Restart.
2023-10-05 | 540 WF 1 | alarm CCP | Check & found emergency switch bad contact. Service & restart.
2023-10-05 | 545 FM 2 | AL10 alarm flow high | Isolate & normalize supply
2023-10-05 | 535 BC 4 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 540 BC 1 | alarm not ready | breakers supply off. Restart.
2023-10-05 | 54B AC 1 | Isolate supply req by Mech. | off MCCB - work done
2023-10-06 | 555 DY 1 | Alarm AO9 | Check found overload breaker trip. Reset.
2023-10-06 | 552 HT 1 | Alarm return fault at CCR | Check found aux contact running. (Return) damage replace. Restart.
2023-10-06 | 561 CP 1 | Trip by alarm element outlet temp. | Isolate & normalize supply
2023-10-07 | 552 SG 3 | Overload | Isolate & normalize supply
2023-10-09 | 561 TR 1 | Maintenance routine | Transformer inspection
2023-10-09 | 54A TR 1 | Maintenance routine | Transformer inspection
2023-10-09 | 54B TR 1 | Maintenance routine | Transformer inspection
2023-10-09 | 545 TR 1 | Maintenance routine | Transformer inspection
2023-10-09 | 552 TR 1 | Maintenance routine | Transformer inspection
2023-10-09 | 545 BM 1 | Operate motor | Isolate & normalize supply
2023-10-09 | 510 BF 2 | Overload | Isolate & normalize supply
2023-10-09 | 54B AC 1 | Not ready | Isolate & normalize supply
2023-10-09 | 510 BF 2 | Overload | Isolate & normalize supply
2023-10-09 | 54B AC 1 | Not ready | Isolate & normalize supply
2023-10-10 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 561 BC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 561 BC 4 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 54A BC 2 | Overload | Isolate & normalize supply
2023-10-10 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 561 BC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 561 BC 4 | Overload | Isolate & normalize supply
2023-10-10 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 562 CP 1 | Overload motor | Isolate & normalize supply
2023-10-10 | 562 CP 2 | Elemet outlet | Isolate & normalize supply
2023-10-11 | 55A BM 1 | Insulation test | Test for motor and starter at CM1 main drive
2023-10-11 | 510 BF 1 | Overload | Isolate & normalize supply
2023-10-11 | 545 FM 1 | Alarm | Isolate & normalize supply
2023-10-11 | 55A BM 1 | Maintenance routine | Blow dust and install heater
2023-10-12 | 561 PG 1 | WO CE 819 - Alarm run line | Service sensor. Tighten cable.
2023-10-12 | 552 SG 3 | Overload | Isolate & normalize supply
2023-10-13 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-13 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-13 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-10-13 | 561 WP 1 FY 1 FII (Flow control gate) | Control Valve (water) cement Mill 4 cannot control auto at CCR. | Replace positioner gate
2023-10-13 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-13 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-13 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-10-14 | 555 DY 1 | Contactor stuck | Replace contactor
2023-10-15 | CCR 2 | PC Cement Mill 3 blank | Rejoint loose cable
2023-10-15 | 552 RP 1 | Maintenance routine | HT Motor Monitoring
2023-10-15 | 552 RP 2 | Maintenance routine | HT Motor Monitoring
2023-10-15 | 545 FN 16 | Maintenance routine | HT Motor Monitoring
2023-10-15 | 546 BM 1 | Maintenance routine | HT Motor Monitoring
2023-10-15 | 561 FN 2 | Maintenance routine | HT Motor Monitoring
2023-10-15 | 561 RL 1 | Maintenance routine | HT Motor Monitoring
2023-10-15 | 561 CL 4 | Classifier lower bearing temp fluctuate | Tighten cable at terminat block. Start back still trip.(fluctuate) during start feed. Trace and suspect joint cable fault.(intermittent) cut and connect back at joint box. Restart.
2023-10-15 | 562 CP 2 | Alarm element outlet temp | Isolate & normalize supply
2023-10-16 | 55A BM 1 | Insulation Test | Stator 0 ohm. Direct short prepare new heater
2023-10-16 | 545 BM 1 | Insulation Test | Spare motor - Starter - 100 mn
2023-10-16 | 561 FN 4 | control breaker trip | Isolate & normalize supply
2023-10-16 | 550 DY 1 | Trip by alarm 409 (overload breaker) | Isolate & normalize supply
2023-10-16 | 550 DY 1 | Alarm A25 "high temp" time starting foam compressor activation not active in standby | Suspect contactor fault. Contactor 24V ac No spare. Check at w/shop found contactor 42V same model swapcoil test ok. Work done
2023-10-17 | 55A BM 1 | Insulation Test | Continue check still short add 1 heater.
2023-10-18 | 55A BM 1 | Insulation Test | Insulation test still short
2023-10-18 | 561 RL 1 | short | Replace 12 pcs c/brush
2023-10-19 | 555 CP 3 | Service request: Isolate supply | Open ACB
2023-10-19 | 55A BM 1 | Insulation Test | Motor stator - still short. Motor cable - 3.5 ohm
2023-10-19 | 540 WF 2 | Maintenance routine | Physical calibration
2023-10-21 | 562 AD 1 | Alarm A25 | Isolate & normalize supply
2023-10-21 | 561 BC 4 | Alarm motion detector | Check and found speed switch out of position. Adjust speed swirch and test ok. start back system.
2023-10-21 | 510 AC 1 | Overload | Isolate & normalize supply
2023-10-23 | 55A BM 1 | Insulation Test | Run motor.
2023-10-23 | 545 BM 1 | Insulation Test | Spare motor
2023-10-23 | 552 SG 3 | Overload | Isolate & normalize supply
2023-10-23 | 552 VV 1 | Breaker control trip | Isolate & normalize supply
2023-10-24 | 545 BM 1 | Service request: Tidy up cable | Spare motor clean water inside motor. Tidy up cable at CM3
2023-10-25 | 545 BM 1 | Service request: Tidy up cable | Tidy up cable
2023-10-26 | 561 RL 1 | Sparking | Check carbon brush
2023-10-26 | 561 BC 4 | WO CE 628 -Local switch not function | Replace local switch
2023-10-26 | 535 BC 5 | Overload | Isolate & normalize supply
2023-10-26 | 561 AL 1 | Rotor short to earth | Dismantle motor
2023-10-26 | 561 RL 105 | Troubleshoot | Disconnect cable & dismantle rotor inching.
2023-10-27 | 54 BC 2 | Overload | Isolate & normalize supply
2023-10-29 | 552 LQ2 TZ2 T02 | Temp. fluctuate | Check found cable loose at PT100. Tighten cable.
2023-10-29 | 561 CP 1 | Miller req to check alarm not ready | Isolate & normalize supply
2023-10-29 | 561 RL 105 | Motor Testing | Run motor.
2023-10-29 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-30 | 561 RL 1 | Motor Testing | Test motor main drive. Free run couple, 100 - 110 kw. 80 Amp / 79 Amp/ 81 Amp (Hyundai)
2023-11-02 | 550 RF 2 | Overload | Isolate & normalize supply
2023-11-04 | 561 GR 1 | Oil pressure low | Check found key master loose. Disconnect cable motor. Repair key motor.
2023-11-04 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2023-11-04 | 540 WF 2 | Alarm belt not feedback | Cannot reset. Req miller to call and check first. Try local. Alarm clear. Restart.
2023-11-05 | 561 GR 1 | Disconnect cable motor | Mech repair welding shaft motor p-up. Rejoint cable & test run.
2023-11-05 | 561 CP 1 | Alarm almost collect | Isolate & normalize supply
2023-11-05 | 562 CP 1 | Fan motor overload | Isolate & normalize supply
2023-11-05 | 561 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-11-05 | 561 GR 3 | Gear recover oil pressure low | Replace 1 pc solenoid valve (No.11). Solenoid valve Part No: DG4V-5-31B-M-PL-D-6-49
2023-11-05 | 562 GR 3 | gear recover oil pressure low | Replace 1 pc solenoid valve. Try start system & monitor, Work together with EE Haziruddin, EE Ikmal, Saifuddin. Solenoid valve part No: DG5V-H8-2A-P2-D-86-JA.
2023-11-05 | 563 GR 3 | Trip | Trip again with same alarm after mill running about 1 hour. * 561 GR01 TP5. *561 GR03M01 P43
2023-11-06 | 561 GR 1 | Troubleshoot | Check found welding crack dismantle motor to w/shop for modification. Modification by Machinist feedback and test ok.
2023-11-06 | 561 GR 3 | Troubleshoot | Gear reducer pump
2023-11-06 | 561 GR 1 | CM4 | Dismantle and install back motor. Modification motor & pump shaft.
2023-11-07 | 552 RP 1 | Maintenance routine (CNY 2024 stoppage) | Monitor for bearing replacing on CNY stopage. Motor c/brush, s/ring and starter for the following motor.
2023-11-07 | 552 RP 1 | Maintenance routine (CNY 2024 stoppage) | Monitor for bearing replacing on CNY stopage. Motor c/brush, s/ring and starter for the following motor.
2023-11-07 | 545 FN 16 | Maintenance routine (CNY 2024 stoppage) | Monitor for bearing replacing on CNY stopage. Motor c/brush, s/ring and starter for the following motor.
2023-11-07 | 545 BM 1 | Maintenance routine (CNY 2024 stoppage) | Monitor for bearing replacing on CNY stopage. Motor c/brush, s/ring and starter for the following motor.
2023-11-07 | 561 FN 2 | Maintenance routine (CNY 2024 stoppage) | Monitor for bearing replacing on CNY stopage. Motor c/brush, s/ring and starter for the following motor.
2023-11-07 | 561 RL 1 | Maintenance routine (CNY 2024 stoppage) | Monitor for bearing replacing on CNY stopage. Motor c/brush, s/ring and starter for the following motor.
2023-11-07 | 552 W 1 | Alarm key not auto | Check cable joint ok. Suspect local switch. Replace local switch ok. After a few minutes miller alarm, trace found cable snape. Cable no 1 and u joint back test ok.
2023-11-09 | 590 VF 1 | New Installation | Vibrating Feeder - Crusher China - Install spare motor and new base. WO CE 843.
2023-11-10 | 552 BI 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-10 | 552 BI 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-10 | 545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-11 | 543 BM 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-11 | 560 FN 1 | Overload | Isolate & normalize supply
2023-11-11 | 561 CP 2 | Alarm overload at CCR | Check at CP alarm service required. Check status alarm DP oil separator service max 0.80 bar. Reset
2023-11-12 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2023-11-12 | 545 FN 16 | Service request: Isolate supply | Isolate & normalize supply
2023-11-12 | 545 SR 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-12 | 545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-12 | 545 BM 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-12 | 562 CP 1 | Overload fan motor | Isolate & normalize supply
2023-11-12 | 562 CP 3 | Element outlet temp. high | Isolate & normalize supply
2023-11-13 | 552 RP 1 | Maintenance routine | Check c/brush - Blow motor, starter and carbon dust at s/ring compartment
2023-11-13 | 552 RP 2 | Maintenance routine | Check c/brush and s/ring condition. Blow motor, starter and carbon dust at s/ring compartment. Replace 2 pcs c.brush
2023-11-13 | 545 FN 16 | Maintenance routine | Check c/brush and s/ring condition. Blow motor, starter and carbon dust at s/ring compartment. Replace 5 pcs c.brush
2023-11-13 | 545 FN 16 | Service request: Isolate supply | Isolate & normalize supply
2023-11-13 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2023-11-14 | 545 SR 3 | Troubleshoot | Connect motor cable and tested
2023-11-14 | 561 RL 1 | Troubleshoot | Fit back cooling Fan ( Old motor)
2023-11-14 | 545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-14 | 545 SR 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-14 | 545 BM 1 | Alarm not ready | Rack in back
2023-11-14 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-17 | 552 PG 2 | WO :CE849 Alarm runtime after select to open | Check and found soleniod valve problem. Replace soleniod valve.
2023-11-18 | 552 PG 2 | WO :CE850 Alarm runtime after mech replace pneumatic Actuators valve | Check and found soleniod valve problem. Replace soleniod valve.
2023-11-18 | 550 FN 1 | Overload | Isolate & normalize supply
2023-11-19 | 555 AL 1 | WO CE851 Blow tank B not discharge | Replace pressure switch
2023-11-19 | 562 CD 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-19 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-11-19 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-19 | T5476 | Show open loop | Tighten cable t/c
2023-11-19 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-19 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-11-19 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-19 | 561 GR 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-20 | 561 BF 2 | Service request: Isolate supply | Isolate & normalize supply
2023-11-20 | 562 CP 1 | Element out let temp high 120 C | Isolate & normalize supply
2023-11-20 | 552 RP 1 | Monitoring | HT Motor Monitoring for the following motor
2023-11-20 | 552 RP 2 | Monitoring | HT Motor Monitoring for the following motor
2023-11-20 | 545 FN 14 | Monitoring | HT Motor Monitoring for the following motor
2023-11-20 | 545 BM 1 | Monitoring | HT Motor Monitoring for the following motor
2023-11-20 | 561 FN 2 | Monitoring | HT Motor Monitoring for the following motor
2023-11-20 | 561 RL 1 | Monitoring | HT Motor Monitoring for the following motor
2023-11-21 | 542 BE 1 | Isolate supply req by mech. | off MCCB
2023-11-21 | 561 RL 1 | Maintenance routine (CNY 2024 stoppage) | Monitor and survey motor for bearing replacement on CNY
2023-11-21 | 552 CP 2 | Trip | Isolate & normalize supply
2023-11-22 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-22 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-11-22 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-22 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-22 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-11-22 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-22 | 561 FN 2 | Short | Replace 8 pcs c/brush. Top up 12 liter distill water for starter. Top up 12 liter distill water for starter.
2023-11-22 | 561 RL 1 | Maintenance routine | Top up 24 liter distill water for starter
2023-11-22 | 561 DA 2 | cable snap | Rejoint cable and restart
2023-11-23 | 54A BM 1 | Insulation test | Inject 6kv - 0 ohm. Inject 1kv - 8 ohm
2023-11-23 | 545 BM 1 | Insulation test | Inject 6kv - 60 ohm. Inject 1kv - 100 ohm
2023-11-23 | 550 CP 1 | Control voltage fuse blow | replace control voltage fuse
2023-11-24 | 562 PP 1 | Valve not function | Replace and service valve
2023-11-24 | 562 CP 2 | Breaker F12 trip | Isolate & normalize supply
2023-11-24 | 552 RP 1 | Reset F12 trip | Isolate & normalize supply
2023-11-25 | 535 BC 6 | Overload | Isolate & normalize supply
2023-11-25 | 550 FN 1 | Overload | Isolate & normalize supply
2023-11-26 | 555 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-26 | 550 FN 1 | Overload coloum 24v error | Replace inverter
2023-11-26 | 550 FN 1 | Schneider panel problem | Change & install back card old panel & spare panel
2023-11-27 | 562 PP 1 | Service request: Check Blow tank A | Check valve. Check pipe. Suspect blockage
2023-11-27 | 555 AL 1 | Blow tank A not function | Check valve. Check found cable coil valve snap. Repair & test.
2023-11-28 | 540 SX 2 | Overload | Isolate & normalize supply
2023-11-28 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-28 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-11-28 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-29 | 552 VV 2 | Alarm run time | Check and found limit switch. Stuck. Service & test.
2023-11-29 | 545 FM 2 | AL 10 flow to high | Isolate & normalize supply
2023-11-30 | 561 RL 1 | Alarm mill liquid starter first step | Isolate & normalize supply
2023-11-30 | 561 RL 1 | Alarm state first step | Isolate & normalize supply
2023-12-02 | 535 BC 6 | Overload | Isolate & normalize supply
2023-12-02 | 552 CP 2 | Trip | Isolate & normalize supply
2023-12-03 | 552 RP 1 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
2023-12-03 | 552 RP 2 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
2023-12-03 | 545 FN 16 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
2023-12-03 | 545 BM 1 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
2023-12-03 | 561 RL 1 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
2023-12-03 | 561 FN 2 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
2023-12-03 | 540 SX 2 | Overload | Isolate & normalize supply
2023-12-03 | 540 BC 1 | Overload | Isolate & normalize supply
2023-12-03 | 540 BC 1 | Alarm motion detector | Check and found speed switch out of position. Calibrate
2023-12-04 | 555 BF 3 | Overload | Isolate & normalize supply
2023-12-04 | 545 FM 2 | AL10 flow too high | Isolate & normalize supply
2023-12-04 | 552 CP 2 | Overload | Isolate & normalize supply
2023-12-05 | 535 BC 4 | Maintenance routine | Greasing the following motor
2023-12-05 | 552 FN 1 | Maintenance routine | Greasing the following motor
2023-12-05 | 552 FN 2 | Maintenance routine | Greasing the following motor
2023-12-05 | 552 BE 1 | Maintenance routine | Greasing the following motor
2023-12-05 | 552 BE 2 | Maintenance routine | Greasing the following motor
2023-12-05 | 542 BE 1 | Maintenance routine | Greasing the following motor
2023-12-05 | 542 BE 2 | Maintenance routine | Greasing the following motor
2023-12-05 | 555 CP 3 | Maintenance routine | Greasing the following motor
2023-12-05 | 552 CP 1 | Maintenance routine | Greasing the following motor
2023-12-05 | 552 CP 2 | Maintenance routine | Greasing the following motor
2023-12-06 | 561 RL 1 | Service request: Isolate supply | Rack out GBC
2023-12-06 | 561 BC 3 | Overload | Isolate & normalize supply
2023-12-06 | 561 BC 3 | Cable speed switch snap (220V) | Rejoint cable and restart
2023-12-06 | 561 CR 2 | Alarm overload at CCR | Check at status DP air filter alarm reset
2023-12-06 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2023-12-06 | 560 BC 3 | Open coil | Check motor. Prepare for motor replacement.
2023-12-06 | 560 BC 3 | Install motor and install new motor | Test run local
2023-12-07 | 560 BC 3 | Service request: Isolate supply | Isolate & normalize supply
2023-12-08 | CM1 | Cable from PL1 to CM1 transformer | Check & megger cable.
2023-12-08 | 535 B 6 | Overload | Isolate & normalize supply
2023-12-11 | 552 LQ 3 | Not show flow at CCR | Check found coil socket snap and 1 cable snap. Replace new socket and cut joint back . Test run -ok
2023-12-11 | Stack 7 | Check at monitor alarm not response | Off and back supply to auto calibrate. Reading at 6.35
2023-12-12 | 561 FN 2 | Troubleshoot | To replaced 3 pcs c/brushes
2023-12-12 | 562 PP 1 | Troubleshoot | Change s/valve
2023-12-12 | 562 PP 2 | Troubleshoot | Change s/valve
2023-12-12 | 555 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 560 BC 1 | Troubleshoot | Load cell prebin
2023-12-12 | 561 BC 1 | Motor abnormal sound | Check test run
2023-12-12 | 555 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 545 FM 2 | AL10 flow too high | Isolate & normalize supply
2023-12-12 | 552 LC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 561 CP 2 | Alarm Dp air filter | Isolate & normalize supply
2023-12-12 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 560 BC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 550 RF 2 | Overload | Isolate & normalize supply
2023-12-12 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 562 CP 1 | Overload from motor | Isolate & normalize supply
2023-12-13 | 552 RP 1 | Maintenance routine | Check carbon brush
2023-12-14 | 561 CP 2 | Breaker for cooling fan damage | Replace breaker
2023-12-14 | 561 CLA 1 | Local switch pole broken | Check found local switch pole broken. Repair.
2023-12-14 | 560 BE 1 | Alarm motion | Check found control breaker 220V Q148 trip reset.
2023-12-15 | 555 CP 3 | Alarm at temp | Isolate supply and normalize supply
2023-12-16 | 560 BF 3 | Overload | Isolate & normalize supply
2023-12-16 | 535 BC 5 | Overload | Isolate & normalize supply
2023-12-16 | 542 BC 4 | Overload | Isolate & normalize supply
2023-12-16 | 561 CP 1 | Overload | Isolate & normalize supply
2023-12-16 | 561 CP 2 | Can't start from CCR | Maintenance fault. Found CP in local mode. Change to remote.
2023-12-17 | 561 CP 2 | Overload fan motor | Isolate & normalize supply
2023-12-19 | 561 PG 1 | WO CE868 Alarm runtime | Check and found solenoid valve problem. Replace solenoid valve and test manual open & close.
2023-12-20 | 555 CP 3 | Service request: Isolate supply | Isolate supply and normalize supply
2023-12-21 | 552 CP 1 | Fault soft start | Isolate supply and normalize supply
2023-12-21 | Stacker Cement Mill | Cannot start | Check and found breaker 220V trip. MCCB 6. Trip cannot reset.Belt cannot reset. Suspect cable short. Follow up needed.
2023-12-22 | 510 GA 3 | Overload | Isolate & normalize supply
2023-12-22 | 510 BA 3 | Overload | Isolate & normalize supply
2023-12-23 | 555 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-12-23 | 545 FM 2 | AL10 flow to figh | Isolate & normalize supply
2023-12-24 | 535 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-12-25 | 552 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2023-12-25 | 552 BE 1 | Overload | Isolate & normalize supply
2023-12-26 | 545 BC 1 | Overload | Isolate & normalize supply
2023-12-26 | 545 RF 1 | Overload | Isolate & normalize supply
2024-12-28 | 561 RL 1 | Rack in GCB | Isolate & normalize supply
2024-12-28 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2024-12-31 | 535 BC 3 | Overload | Isolate & normalize supply
2024-12-31 | 535 BC 6 | Overload | Isolate & normalize supply
2024-01-01 | 552 RP 1 | Monitoring | HT Motor monitoring, motor c/brush, s/ring and starter condition.
2024-01-01 | 552 RP 2 | Monitoring | HT Motor monitoring, motor c/brush, s/ring and starter condition.
2024-01-01 | 545 FN 16 | Monitoring | HT Motor monitoring, motor c/brush, s/ring and starter condition.
2024-01-01 | 545 BM 1 | Monitoring | HT Motor monitoring, motor c/brush, s/ring and starter condition.
2024-01-01 | 561 FN 2 | Monitoring | HT Motor monitoring, motor c/brush, s/ring and starter condition.
2024-01-01 | 561 RL 1 | Monitoring | HT Motor monitoring, motor c/brush, s/ring and starter condition.
2024-01-03 | CM1 | Service request: Isolate supply | Rack in GCB
2024-01-03 | CM3 ER 7 | Trip incoming VCB | Close VCB
2024-01-03 | CM1 | Insulation test | Test for transformer. R-E: 700, Y-E: 700, B-E: 700
2024-01-03 | CM2 | cable punctured | Incoming Line 1 trip at MTS. Connect cable and normalize supply. Check and found cable CM1 transformer punctured behind CM2 w/feeder room.
2024-01-03 | CM3 | Insulation test | Test for transformer. R-E: 1.4 ohm, Y-E: 1.4 ohm, B-E: 1.4 ohm
2024-01-03 | CM4 | Insulation test | Test for cable main drive. R-E: 100 ohm, Y-E: 50 ohm, B-E: 25 ohm, R-Y: 14 ohm, R-B: 14 ohm, Y-B: 16 ohm
2024-01-03 | 545 FM 1 | AL10 flow to high | Isolate & normalize supply
2024-01-04 | 590 VF 1 | Motor Testing | To test motor. Motor rated 22A (hopper empty) R-38 A, Y-37.9 A, B-38 A
2024-01-04 | 590 VF 1 | Try release spring tension and test | R-30 A, Y-30.2 A, B-30.5 A
2024-01-04 | 590 VF 1 | Troubleshoot | Reposition motor and modified base motor test. R-21.5 A, Y-21.7 A, B-22 A
2024-01-04 | 590 VF 1 | Gearbox problem | R-23 A, Y-23 A, B-23 A. After few minute motor trip on 23 A O/L setting 24A. To be continue test due to 590 BC 1 gear box problem. Disconnect cable motor 590 BC 1
2024-01-05 | 542 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-01-05 | 54A FA 2 | Overload | Reset still not ok, Check and weight motor amp old ohm same. Check motor bearing stuck. Motor dismantle and already to workshop.
2024-01-06 | 54A FA 2 | New Installation | Install coupling at new motor. Install motor connect cable alignment. Test rotation and pleasure amp.
2024-01-06 | 54A FA 2 | Trip alarm A28 | Silo 1-1. Assist group shift to install motor
2024-01-08 | 562 AD 1 | Trip alarm A28 | Isolate & normalize supply
2024-01-08 | 561 FN 2 | short | Check c/brush. Top up 20 liter distill water for starter due to low level.
2024-01-08 | 561 RL 1 | maintenance routine | Check c/brush , s/ring and starter
2024-01-08 | 590 VF 1 | Test run | R-25.5, Y-25.5 , B-25.5
2024-01-08 | 590 VF 1 | After release spring | R-23.5, Y-23.5 , B-23.5
2024-01-08 | 590 VF 1 | motor overheat | Test free run 16A. Motor rated 22A.
2024-01-09 | 552 GA 1 | gate stuck | Isolate & normalize supply
2024-01-09 | 545 BM 1 | Insulation test | Test for spare motor. Starter R-E: 70 ohm, Y-E: 70 ohm, B-E: 70 ohm
2024-01-09 | 545 BM 1 | Insulation test | Test for spare motor. Starter R-E: 12 ohm, Y-E: 12 ohm, B-E: 12 ohm
2024-01-10 | 54A LP 1 | Insulation low and bearing jammed. | Service HEMT winding
2024-01-10 | 545 BM 1 | Motor Testing | Spare motor prepare space to relocate motor at warehouse.
2024-01-10 | 562 CP 1 | Overload fan motor | Isolate & normalize supply
2024-01-10 | 562 CP 1 | Isolate supply | Off MCCB
2024-01-10 | 562 CP 2 | Isolate supply | Off MCCB
2024-01-10 | 562 CP 3 | Isolate supply | Off MCCB
2024-01-11 | 510 AC 1 | Overload | Isolate & normalize supply
2024-01-11 | 510 AC 1 | Service request: Isolate supply | Isolate & normalize supply
2024-01-15 | CM1 | Transformer insulation test. | R: 900 ohm, Y: 900 ohm, B: 900 ohm
2024-01-15 | CM1 | Insulation test | Test for cable. R-E: 30 ohm, Y-E: 140 ohm, B-E: 100 ohm. Rejoint cable.
2024-01-15 | 54A LP 1 | New Installation | Reassemble motor. Replace 2 pcs bearing 6205 ZZ. Test run. R: 1.4 A, Y: 1.4 A, B: 1.5A. Motor 1.1 KW.
2024-01-15 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2024-01-15 | 562 CP 1 | Overload fan motor | Isolate & normalize supply
2024-01-17 | CM1 | Insulation test | Test for transformer. R-E: 1 ohm , Y-E: 1 ohm, B-E: 1 ohm
2024-01-17 | CM1 | cable punctured | 4 meter from join. Connect back supply from CM2 to CM1. Rack out incoming ACB CM1.
2024-01-17 | 545 BM 1 | Insulation test | Test for spare motor.
2024-01-17 | 535 BC 6 | Overload | Isolate & normalize supply
2024-01-18 | 552 RP 1 | maintenance routine | Check motor , carbon brush, s/ring and starter
2024-01-18 | 552 RP 2 | maintenance routine | Check motor , carbon brush, s/ring and starter
2024-01-19 | CM3 | WO: CE 879 : Miller request to check group. Group 545 and 535 trip. | Check at ER5 trip incoming. Check and found breaker for 545 FN 13 trip. Perform insulation test at terminal, result show motor short. Replace motor and test.
2024-01-19 | 545 FN 13 | Motor short | 15KW, 4 pole, 27.5 A. Taken record motor at workshop for replacement test run with fan. R-19-5 A, Y-19-5 A, B-19-4 A. Hand over to planner for alignment.
2024-01-19 | 550 FN 1 | New Installation | Install stopper and alignment panel inverter.
2024-01-21 | 552 BC 4 | Overload | Isolate & normalize supply
2024-01-22 | 552 RP 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-01-22 | 552 RP 2 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-01-22 | 545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-01-22 | 545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-01-22 | 561 FN 2 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-01-22 | 561 RL 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-01-22 | 542 BC 4 | Monitoring | Remonitoring LV Motor for bearing replacement on CNY.
2024-01-22 | 520 BC 8 | Monitoring | Remonitoring LV Motor for bearing replacement on CNY.
2024-01-22 | 550 BF 3 | Monitoring | Remonitoring LV Motor for bearing replacement on CNY.
2024-01-23 | 562 CP 1 | Isolate supply | Isolate & normalize supply
2024-01-23 | 562 CP 2 | Isolate supply | Isolate & normalize supply
2024-01-23 | 562 CP 3 | Isolate supply | Isolate & normalize supply
2024-01-23 | 561 CP 1 | Alarm | Isolate & normalize supply
2024-01-23 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-01-23 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-01-23 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-01-25 | 562 CP 1 | Overload from motor | Isolate & normalize supply
2024-01-28 | 562 AD 1 | Alarm A25 | Isolate & normalize supply
2024-01-29 | 55 B1 T1 | GCB always closing | Service
2024-01-29 | 545 BM 1 | Insulation test | Test for spare motor. Stator - R-E: 70 M ohm, Y-E: 70 M ohm, B-E: 70 M ohm
2024-01-29 | 545 BM 1 | Insulation test | Test for spare motor. Rotor - R-E: infiniti, Y-E: infiniti, B-E: infiniti
2024-01-29 | 55B 1T1 | GBC cannot tripping | Replace tripping coil for 55B 1T1 (CM2)
2024-01-29 | 562 CP 1 | Overload fan motor | Isolate & normalize supply
2024-01-29 | 561 CP 1 | Return fault at CCR | Check at Panel CP alarm starter feedback contact. Reset. Restart still return fault. Contactor not energize. Indicator " Comp run" at controller showing run. Attendant check oil leak. Try local motor still not run. Suspect safety sensor out off or controller problem. Need to follow up - trip.
2024-01-30 | 561 CP 2 | Not load | Disconnect, cut & rejoint cable.
2024-01-30 | 545 FN 4 | Isolate supply | Isolate & normalize supply
2024-01-30 | 545 FN 20 | Isolate supply | Isolate & normalize supply
2024-01-30 | 545 BM 1 | Isolate supply | Isolate & normalize supply
2024-01-30 | 561 BC 1 | Isolate supply | Isolate & normalize supply
2024-01-30 | 561 BC 4 | Isolate supply | Isolate & normalize supply
2024-01-30 | 552 FN 2 | Not ready | Isolate & normalize supply
2024-01-31 | 561 BC 4 | Overload | Isolate & normalize supply
2024-01-31 | 561 CP 2 | Socker valve problem | Repair socker valve
2024-01-31 | 562 AD 1 | Alarm 411, A09 | Isolate & normalize supply
2024-01-31 | 561 CP 1 | open switch | By pass temp switch
2024-01-31 | 54A BM 1 |  | Lay cable (fly) from MCC CM1, to main drive motor and to winding motor for heating. Motor already baricate. Amp - R-3.2A. Y-3.2A, B-3.2A.
2024-01-31 | 550 RF 2 | Overload | Isolate & normalize supply
2024-01-31 | 562 AD 1 | Dryer alarm A25 | Isolate & normalize supply
2024-02-01 | 552 RP 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-02-01 | 552 RP 2 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-02-01 | 545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-02-01 | 545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-02-01 | 561 FN 2 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-02-01 | 561 RL 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-02-01 | 552 RP 1 | short | Replace 1 pc carbon brush
2024-02-01 | 562 AD 1 | Service request: Dryer check. Alarm A25 | Off & restart Dryer. Test ok
2024-02-01 | 552 CP 2 | Overload | Isolate & normalize supply
2024-02-02 | 54A BM 1 | Insulation test | Insert 6KV R-E- 0 M ohm, Y-E- 0 M ohm , B-e- 0 M ohm
2024-02-02 | 54A BM 1 | Insulation test | Insert 1 KV R-E- 15 M ohm, Y-E- 15 M ohm , B-E- 15 M ohm
2024-02-03 | 552 RP 1 | CE 885. Return fault | Check at panel VCB trip. Check motor found carbon crush sparking. Rack out VCB. Dismantlr carbon brush and holder. Megger : stator. Normal group continue skin slip ring-inprogress.
2024-02-03 | 552 RP 1 | Roller press motor CM3 | Checking motor.
2024-02-03 | 552 RP 1 | Roller press motor CM3 | Motor stationary site failure suspect carbon brush stuck holder cause sparking on slip ring.
2024-02-03 | 552 RP 1 | Monitoring | Visual inspection
2024-02-04 | 552 RP 1 | short | Check carbon brush and ring on stationary motor. Replace 1 pc carbon brush on movable motor
2024-02-04 | 552 RP 1 | short | Replace 1 pc carbon brush on movable motor
2024-02-05 | 552 RP 1 | Maintenance routine | Greasing motor
2024-02-05 | 552 RP 2 | Maintenance routine | Greasing motor
2024-02-05 | 561 FN 1 | Maintenance routine | Greasing motor
2024-02-05 | 561 FN 2 | Maintenance routine | Greasing motor
2024-02-05 | 561 RL 1 | Maintenance routine | Greasing motor
2024-02-05 | 561 CLA 1 | Maintenance routine | Greasing motor
2024-02-05 | 560 FN 1 | Maintenance routine | Greasing motor
2024-02-05 | 561 FN 3 | Maintenance routine | Greasing motor
2024-02-05 | 561 RL 1 | Maintenance routine | Greasing motor
2024-02-05 | 552 RP 1 | Maintenance routine | Check carbon brush & slip ring condition
2024-02-05 | 552 RP 2 | Maintenance routine | Check spring tension, carbon brush loosenes & starter condition
2024-02-06 | 561 TR 1 | Monitoring | Transformer inspection
2024-02-06 | 54A TR 1 | Monitoring | Transformer inspection
2024-02-06 | 54B TR 1 | Monitoring | Transformer inspection
2024-02-06 | 545 TR 1 | Maintenance routine | Transformer inspection
2024-02-06 | 552 TR 1 | Monitoring | Transformer inspection
2024-02-06 | 54A BM 1 | Troubleshoot | Disconnect cable supply for heating and bring to work shop
2024-02-06 | 535 BC 1 | Motor abnormal sound | Monitor bearing motor condition
2024-02-07 | 552 RP 1 | Maintenance routine (CNY 2024 stoppage) | Check carbon brush & slip ring contition ok. Check spring tension, carbon brush loosenes ok
2024-02-07 | 552 RP 2 | Maintenance routine (CNY 2024 stoppage) | Check carbon brush and slip ring contition ok. Check spring tension, carbon brush loosenes ok
2024-02-08 | 552 PP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-08 | 545 BM 1 | Isolate supply | Rack out GCB/VCB
2024-02-08 | 545 FN 16 | Isolate supply | Rack out GCB/VCB
2024-02-08 | 552 RP 1 | Isolate supply | Rack out GCB/VCB
2024-02-08 | 552 RP 2 | Isolate supply | Rack out GCB/VCB
2024-02-08 | 545 FN 14 | Isolate supply | Open ACB. Rack out.
2024-02-08 | 555 CP 3 | Isolate supply | Open ACB. Rack out.
2024-02-08 | 542 BE 1 | Isolate supply | Off MCCB
2024-02-08 | 552 BE 1 | Isolate supply | Off MCCB
2024-02-08 | 552 BE 2 | Isolate supply | Off MCCB
2024-02-08 | 540 BC 1 | Isolate supply | Off MCCB
2024-02-08 | 540 BC 2 M01 | Isolate supply | Off MCCB
2024-02-08 | 552 BE 1 M02 | Isolate supply | Off MCCB
2024-02-08 | 552 BE 2 M02 | Isolate supply | Off MCCB
2024-02-08 | 545 SR 1 | Isolate supply | Off MCCB
2024-02-08 | 545 SR 3 | Isolate supply | Off MCCB
2024-02-08 | 545 FN 15 | Isolate supply | Off MCCB
2024-02-08 | 545 SR 3 | Disconnect cable motor. | Work done
2024-02-08 | 545 FN 7 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 552 FN 7 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 545 FN 6 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 545 FN 8 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 550 BF 3 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 545 BF 2 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 542 BC 4 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 520 BC 8 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 545 FN 7 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 552 FN 7 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 545 FN 6 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 550 BF 3 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 545 BF 2 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 542 BC 4 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 520 BC 8 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 552 LQ 1 | Maintenance routine (CNY 2024 stoppage) | Dismantle , service and install motor. Bearing No: LS: 6205ZZ, WO: EE 778
2024-02-08 | 552 LQ 1 | Maintenance routine (CNY 2024 stoppage) | Dismantle , service and install motor. Bearing No: OLS: 6204ZZ
2024-02-08 | 552 LQ 2 | Maintenance routine (CNY 2024 stoppage) | Dismantle , service and install motor. Bearing No: LS: 6305ZZ WO: EE 779
2024-02-08 | 552 LQ 2 | Maintenance routine (CNY 2024 stoppage) | Dismantle , service and install motor. Bearing No: OLS: 6204ZZ
2024-02-08 | 545 FN 1 | Maintenance routine (CNY 2024 stoppage) | Dismantle , service and install motor. Bearing No: LS: 6308ZZ WO: EE774
2024-02-08 | 545 FN 1 | Maintenance routine (CNY 2024 stoppage) | Dismantle , service and install motor. Bearing No: OLS: 6208ZZ
2024-02-08 | 545 FN 7 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6308
2024-02-08 | 545 FN 7 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6208
2024-02-08 | 552 FN 7 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6308
2024-02-08 | 552 FN 7 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6306
2024-02-08 | 545 FN 6 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6308
2024-02-08 | 545 FN 6 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6208
2024-02-08 | 545 FN 8 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6308
2024-02-08 | 545 FN 8 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6208
2024-02-08 | 550 BF 3 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6208
2024-02-08 | 550 BF 3 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6205
2024-02-08 | 545 BF 2 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6207
2024-02-08 | 545 BF 2 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6206
2024-02-08 | 542 BC 4 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6307
2024-02-08 | 542 BC 4 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6206
2024-02-08 | 520 BC 8 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6206
2024-02-08 | 520 BC 8 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6205
2024-02-08 | 545 FN 10 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6308
2024-02-08 | 545 FN 10 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6208
2024-02-09 | 561 CP 2 | Alarm overload at CCR | Check at CP alarm. Service DP air filter
2024-02-09 | 542 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-09 | 542 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-09 | 562 AD 1 M01 | Alarm A25 | Isolate & normalize supply
2024-02-09 | Blow tank CM3 | Service request: Exhaust valve | Disconnect cable (220V)
2024-02-09 | 552 BE 2 M02 | Normalize fuse form | On MCCB
2024-02-09 | 552 CP 1 | Isolate supply | Off MCCB (Isolator)
2024-02-09 | 552 CP 2 | Isolate supply | Off MCCB (Isolator)
2024-02-09 | 540 WP 2 | Isolate supply | Off overload breaker
2024-02-09 | 542 BC 4 | Isolate supply | Off MCCB
2024-02-09 | 555 CP 3 | Isolate supply | Off MCCB
2024-02-09 | 535 BC 1 | Isolate supply | Off MCCB. Work done
2024-02-09 | 540 BC 1 | Normalize supply | On MCCB
2024-02-09 | 545 FN 7 | Maintenance routine (CNY 2024 stoppage) | Motor LV Maintenance - Service motor. Install motor at site. WO EE 765
2024-02-09 | 552 FN 7 | Motor LV Maintenance - Service motor. Install motor at site. WO EE 776 | Cement Mill & Packing CNY 2024 stoppage
2024-02-09 | 545 FN 6 | Maintenance routine (CNY 2024 stoppage) | Motor LV Maintenance - Service motor. Install motor at site. WO EE 766
2024-02-09 | 550 BF 3 | Motor LV Maintenance - Service motor. Install motor at site. WO EE 777 | Cement Mill & Packing CNY 2024 stoppage
2024-02-09 | 545 BF 2 | Maintenance routine (CNY 2024 stoppage) | Motor LV Maintenance - Service motor. Install motor at site. WO EE 769
2024-02-09 | 545 FN 13 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor and service .WO : EE 765
2024-02-09 | 545 FN 8 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor and service .WO : EE 767
2024-02-09 | 545 FN 10 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor and service .WO : EE 773
2024-02-09 | 542 BC 4 | Maintenance routine (CNY 2024 stoppage) | ContInue service motor WO : EE 770/ oil seal
2024-02-09 | 520 BC 5 | Maintenance routine (CNY 2024 stoppage) | ContInue service motor WO : EE 772
2024-02-09 | 545 FN 7 | Installation | Install and dismantle motor CM3 - complete
2024-02-09 | 552 FN 7 | Installation | Install and dismantle motor CM3 - complete
2024-02-09 | 545 FN 6 | Installation | Install and dismantle motor CM3 - complete
2024-02-09 | 550 BF 3 | Installation | Install and dismantle motor CM3 - complete
2024-02-09 | 545 BF 2 | Installation | Install and dismantle motor CM3 - complete
2024-02-09 | 545 FN 10 | Installation | Install and dismantle motor CM3 - Ready to install. After completing the service do an insulation test
2024-02-09 | 520 BC 8 | Installation | Install and dismantle motor CM3 - Ready to install. After completing the service do an insulation test
2024-02-09 | 542 BC 4 | Installation | Install and dismantle motor CM3 - Ready to install. After completing the service do an insulation test
2024-02-09 | 545 FN 13 | Installation | Install and dismantle motor CM3 - Ready to install. After completing the service do an insulation test
2024-02-09 | 545 FN 8 | Installation | Install and dismantle motor CM3 - Ready to install. After completing the service do an insulation test
2024-02-10 | 552 BE M02 | Normalize supply | On MCCB
2024-02-10 | 552 BE M01 | Normalize fuse form | On MCCB
2024-02-10 | 552 BE M01 | Normalize fuse form | On MCCB
2024-02-10 | 535 VV 4 | New Installation (gate) | Install sensor close/open. Test signal open/close. Replace valve.Test local cannot operate. By pass piping still cannot open. Suspect gate stuck. Follow up needed. 19.7.2. Open. 19.7.3.Close. Command: 22.3.4
2024-02-10 | 545 FN 15 | Service request: Isolate supply | Isolate & normalize supply
2024-02-10 | 561 RL 1 M03 | Isolate supply | Off MCCB. Work done
2024-02-10 | 560 BC 1 | Isolate supply | Off MCCB. Work done
2024-02-10 | 561 BC 3 | Isolate supply | Off MCCB. Work done
2024-02-10 | 561 BC 4 | Isolate supply | Off MCCB. Work done
2024-02-10 | 545 FN 10 | Installation | Install motor CM3
2024-02-10 | 520 BC 8 | Installation | Install motor CM4
2024-02-10 | 542 BC 4 | Installation | Install motor CM5
2024-02-10 | 545 FN 8 | Installation | Install motor CM3
2024-02-10 | 545 FN 15 | Installation | Install motor CM3
2024-02-10 | 54A BM 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 55A TR 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 54B BM 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 55B TR 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 545 TR 1 | Maintenance routine | Cleaning TX room and TX
2024-02-10 | 552 TR 1 | Maintenance routine | Cleaning TX room and TX
2024-02-10 | 545 FN 16 | Installation | Install motor at site
2024-02-10 | 545 FN 8 | Installation | Install motor at site
2024-02-10 | 545 FN 10 | Installation | Install motor at site
2024-02-10 | 542 BC 4 | Installation | Install motor at site
2024-02-10 | 520 BC 8 | Installation | Install motor at site
2024-02-10 | 545 TR 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 552 TR 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 54A BM 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 560 TR 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 545 BM 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 54B TR 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 54B BM 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 54B TR 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | CM3 | Hoist not function | Check found supply. Genset not running. Genset problem 2x stop. Follow up needed.
2024-02-10 | 510 BE 1 | Isolate supply | Work done
2024-02-10 | 510 BE 2 | Isolate supply | Work done
2024-02-10 | 535 AC 1 | Isolate supply | Work done
2024-02-10 | 545 SR 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-10 | 545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-10 | 555 CP 3 | Normalize fuse form | On MCCB
2024-02-10 | 542 BE 2 | Normalize fuse form | On MCCB
2024-02-10 | 535 BC 1 | Normalize fuse form | On MCCB
2024-02-10 | 510 BE 2 | Normalize fuse form | On MCCB
2024-02-10 | 510 BE 1 | Normalize fuse form | On MCCB
2024-02-10 | 561 RL 1 | Service request: Isolate supply | VCB cannot work-out. Power cut off control breaker. Rack-out after power cut.
2024-02-10 | 545 SC 1 | Cover fan out position / motor no cooling fan | Install fan take from workshop and fix back cover fan.
2024-02-10 | 552 RP 1 | Check siren start warning | Check out put, relay output and supply 220V. Follow up needed.
2024-02-10 | 552 RP 2 | Check siren start warning | Check out put, relay output and supply 220V. Follow up needed.
2024-02-10 | 545 BM 1 | Check siren start warning | Check output, relay output and supply 220V. Follow up needed.
2024-02-11 | 545 FN 16 | Maintenance routine | WO: EE718. Motor and starter maintenance. Blow motor, slip ring and filter. IR test starter . R-E: 5 KV. Y-E: 5KV. B-E: 5KV. Lift up resistance starter and check all contact and resistor. Dismantle all fixed and moving contact bring back to workshop. Repair and service all the contact piece. Reinstall to starter, cleaning and renew oil.
2024-02-11 | 545 FN 16 | Maintenance routine | WO: EE718. Motor and starter maintenance. Blow motor, slip ring and filter. IR test rotor . R-E: 1 KV. Y-E: 1 KV. B-E: 1 KV. Lift up resistance starter and check all contact and resistor. Dismantle all fixed and moving contact bring back to workshop. Repair and service all the contact piece. Reinstall back to starter, cleaning and renew oil.
2024-02-11 | 545 FN 16 | Maintenance routine | Maintenance motor 545 FN 16 and starter. Insulation test starter 5 KV - 30 ohm - 3 minutes. Insulation test rotor 1 KV- Infinity 3 minutes. Replace oil starter 350 liter. Replace moving contact 6 pcs for start point and flatten the damaged all contact.
2024-02-11 | CM3 | Siren Mill. Siren roller press | Replace new siren. Siren roller press test.
2024-02-12 | 535 BC 9 | Normalize supply | On MCCB
2024-02-12 | 561 BC 4 | Normalize supply | On MCCB
2024-02-12 | 561 BC 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | 561 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | 560 BC 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | 561 BC 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | 561 RL 1 | Normalize fuse form | On MCCB
2024-02-12 | 561 BC 4 | Normalize fuse form | On MCCB
2024-02-12 | 560 BC 1 | Normalize fuse form | On MCCB
2024-02-12 | 561 BC 3 | Normalize fuse form | On MCCB
2024-02-12 | 545 FN 15 | Normalize fuse form | On MCCB
2024-02-12 | CM3 (Siren) | Not function | Check and troubleshoot. Supply okay. 220V. (Relay WN9 Siren). Relay WN 10 lamp. Replace new siren. Test. Siren: 13.6.1. Lamp:13.6.2.
2024-02-12 | 561 RL 1 | Normalize supply | On MCCB
2024-02-12 | CM3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | CM3 | Lay cable for main drive CM3 - damaged | Prepare for cable pointer. Follow up needed.
2024-02-12 | 535 BC 9 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | 561 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | 535 AC 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 545 BE 1 | Isolate supply | Isolate & normalize supply
2024-02-13 | 540 BC 1 | Isolate supply | Isolate & normalize supply
2024-02-13 | 540 BC 2 | Isolate supply | Isolate & normalize supply
2024-02-13 | 542 BC 1 | Isolate supply | Isolate & normalize supply
2024-02-13 | 55B ITI Dept | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | CM3 (Exhaust valve blow tank) | A site: Cable snap | B site: Rejoint cable
2024-02-13 | 555 CP3 | Service request: Isolate supply | Rack in ACB
2024-02-13 | 510 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 510 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 542 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 542 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 562 AD 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 552 CP 3 | Not working | Check coil valve load unload
2024-02-13 | 545 BM1 | Cable punctured | Cut and reroute main drive cable. Training job have been carry on by cable jointer. Uncouple motor and test rotation. Amp per phase at power meter.
2024-02-13 | 545 FN 16 | Cable punctured | Cut and reroute cable. Jointing job have been carry on by cable jointer (Semmy). Cable size 16mm 3C XLPE
2024-02-13 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 545 SR 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 545 BM 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 542 BC 4 | Overload 4x | Isolate & normalize supply
2024-02-13 | 545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 561 RL 01 | Isolate supply | Isolate & normalize supply
2024-02-13 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 545 SR 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 545 BM 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 542 BC 4 | Overload 4x | Isolate & normalize supply
2024-02-13 | 545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 561 RL 1 | Isolate supply | Isolate & normalize supply
2024-02-13 | 510 BC 1 | Motion | Adjust speed switch. Test.
2024-02-13 | 540 BC 2 | Motion | Adjust speed switch. Test.
2024-02-13 | 545 FN 15 | Motor Testing | Test rotation for motor
2024-02-13 | 545 FN 10 | Motor Testing | Test rotation for motor
2024-02-13 | 545 FN 16 | Motor Testing | Test run control for starter position
2024-02-13 | 545 BM 1 | Cable punctured | Uncouple motor and test rotation. Amp per phase of power meter. L1: 11A, L2: 1A, L3: 12A. Low per phase at power meter, L1:17KW, L2:10KW, L3:18KW.
2024-02-13 | 545 FN 16 | Cable punctured | Cut and reroute cable. Joining job have been calling on by cable jointer. Cable saiz 16mm 3C XCPE.
2024-02-13 | 545 FN 15 | Cable at terminal MCC burn | Cut & rejoint
2024-02-13 | 545 FN 16 | Insulation test | Insulation test cable, after jointer finish. Start local for test rotation
2024-02-14 | 552 RP 1 | HT Motor monitoring, monitor carbon brush, slip ring and starter condition | All motor are in good condition.
2024-02-14 | 552 RP 2 | HT Motor monitoring, monitor carbon brush, slip ring and starter condition | All motor are in good condition.
2024-02-14 | 545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-14 | 545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-14 | 552 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-14 | 555 DY 1 | Alarm A01 -HP. Alarm A09 - Compressor overload. | Blow panel. Service aux contact service pressure switch. Reset pressure switch. Alarm clear. Test.
2024-02-15 | 510 AC 1 | maintenance routine | Greasing motor
2024-02-15 | 552 RP 1 | maintenance routine | Greasing motor
2024-02-15 | 552 RP 2 | maintenance routine | Greasing motor
2024-02-15 | 545 FN 12 | maintenance routine | Greasing motor
2024-02-15 | 545 FN 4 | maintenance routine | Greasing motor
2024-02-15 | 552 PP 1 | maintenance routine | Greasing motor
2024-02-15 | 550 FN 1 | maintenance routine | Greasing motor
2024-02-15 | 545 FN 14 | maintenance routine | Greasing motor
2024-02-15 | 545 FN 16 | maintenance routine | Greasing motor
2024-02-15 | 545 SR 3 | maintenance routine | Greasing motor
2024-02-15 | 545 SR 1 | maintenance routine | Greasing motor
2024-02-15 | 535 BC 4 | maintenance routine | Greasing motor
2024-02-15 | 552 FN 1 | maintenance routine | Greasing motor
2024-02-15 | 552 FN 2 | maintenance routine | Greasing motor
2024-02-15 | 552 PG 2 | Service request: check gate open 30% only at CCR | Check at site gate open 60%. Found part looser. Tighten back. Test.
2024-02-15 | 535 BC 5 | Alarm not ready | Isolate & normalize supply
2024-02-16 | 562 CP 1 | Isolate supply | Done
2024-02-16 | 562 CP 2 | Isolate supply | Done
2024-02-16 | 562 CP 3 | Isolate supply | Done
2024-02-16 | 532 CP 3 | Isolate supply | Done
2024-02-16 | 5632 AD 1 | Trip breaker overload | Check found compressor problem. Coil unbalance RB 3.2 BY 19.2 RY 19.2 Ohm
2024-02-16 | 552 RP 1 | Calibration | Calibrate gap sensor
2024-02-16 | 552 RP 1 ZZ1Z01 | Calibration | Calibrate Gap sensor position left/Right
2024-02-16 | 552 RP 1 ZZ1Z02 | Calibration | Calibrate Gap sensor position left/Right
2024-02-16 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-16 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-16 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-16 | 545 FN 4 | Service request: Isolate supply | Rack ACB & close
2024-02-16 | 545 FN 1 | Reading not showing at CCR | Check alarm. AL60 AD fail. Reset.
2024-02-17 | 562 AD 1 Drayer Cement Mill 4 | Alarm A09 | Check and found overload breaker trip. Reset.
2024-02-18 | 562 AD 1 Drayer Cement Mill 4 | Trip alarm A09 | Reset overload breaker.
2024-02-19 | 552 RP 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-19 | 552 RP 2 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-19 | 545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-19 | 545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-19 | 561 FN 2 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-19 | 561 RL 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-19 | 545 FN 15 | Monitoring | Cleaning motor body for bearing replacement. Follow up needed.
2024-02-19 | 555 AL 1 | CM3 (Blow tank B cannot discharge) | Service and adjust breaket limit switch receiver (A). Test run.
2024-02-19 | 552 CP 1 | Safety interlock | Isolate & normalize supply
2024-02-19 | 545 BC 1 | Overload | Isolate & normalize supply
2024-02-19 | 552 RP 1 | Machine fault | Reset starter.
2024-02-20 | 552 LQ 3 | Service request: to check alarm level SW | Check grease at tank. Try start manual. No alarm. Check pressure switch & test. Found pressure switch & test.
2024-02-20 | 542 BC 4 | Overload | Isolate & normalize supply
2024-02-20 | 545 FN 15 | Winding motor full of grease | Cleaning
2024-02-20 | 552 LQ 3 | Alarm level low | Check found pressure switch problem. Taken record pressure switch at Mechanical workshop. Test.
2024-02-21 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-21 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-21 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-21 | 542 BE 1 | maintenance routine | Greasing the following motor
2024-02-21 | 542 BE 2 | maintenance routine | Greasing the following motor
2024-02-21 | 552 BE 1 | maintenance routine | Greasing the following motor
2024-02-21 | 552 BE 2 | maintenance routine | Greasing the following motor
2024-02-21 | 555 CP 3 | maintenance routine | Greasing the following motor
2024-02-21 | 552 CP 1 | maintenance routine | Greasing the following motor
2024-02-21 | 552 CP 2 | maintenance routine | Greasing the following motor
2024-02-21 | 562 CP 3 | maintenance routine | Greasing the following motor
2024-02-21 | 561 CP 1 | maintenance routine | Greasing the following motor
2024-02-21 | 561 CP 2 | maintenance routine | Greasing the following motor
2024-02-21 | 562 CP 1 | maintenance routine | Greasing the following motor
2024-02-21 | 562 CP 2 | maintenance routine | Greasing the following motor
2024-02-21 | 562 CP 3 | maintenance routine | Greasing the following motor
2024-02-21 | 561 FN 2 | maintenance routine | Monitor carbon brush and slip ring. Top up 12 liter distill water for starter
2024-02-21 | 561 RL 1 | maintenance routine | Monitor carbon brush and slip ring. Top up 12 liter distill water for starter
2024-02-21 | 562 AD 1 | Check alarm 23:Temp. Low | Isolate & normalize supply
2024-02-21 | 562 CP 1 | Service request: Isolate supply | ON MCCB
2024-02-21 | 562 CP 2 | Service request: Isolate supply | ON MCCB
2024-02-21 | 562 CP 3 | Service request: Isolate supply | ON MCCB
2024-02-21 | 562 AD 1 | Alarm A23. Temp Low | EE Azim request adjust by pass hot gas valve (VB).Temp showing. 0.7 C - 5 C. Still monitor. Inform to EE Azim.
2024-02-22 | 54A LP 1 | Motor Testing | Test motor at workshop after bearing replacement. R-1.6, Y-1.7, B-1.7 .Install at site. Need to test rotation
2024-02-23 | 535 BC 7 | Insulation test | R-150. Y-150 B-151
2024-02-23 | 54A AS 1 | Motor Testing | Test local run - condition ok.
2024-02-23 | 54A AS 2 | Motor Testing | Test local run - condition ok.
2024-02-23 | 54A DA 1 | Motor Testing | Test local run - condition ok.
2024-02-23 | 54A WP 2 | Insulation test | R-200. Y-200 B-201
2024-02-23 | 54A WF 1 | Insulation test | R-250. Y-250 B-250
2024-02-23 | 54A WF 2 | Insulation test | R-250. Y-250 B-250
2024-02-23 | 54A WF 3 | Insulation test | R-200. Y-200 B-201
2024-02-26 | 552 RP 1 | Monitoring | HT Motor monitoring , Monitor carbon brush. Slip ring and starter condition
2024-02-26 | 552 RP 2 | Monitoring | HT Motor monitoring , Monitor carbon brush. Slip ring and starter condition
2024-02-26 | 545 FN 16 | Monitoring | HT Motor monitoring , Monitor carbon brush. Slip ring and starter condition
2024-02-26 | 545 BM 1 | Monitoring | HT Motor monitoring , Monitor carbon brush. Slip ring and starter condition
2024-02-26 | 561 FN 2 | Monitoring | HT Motor monitoring , Monitor carbon brush. Slip ring and starter condition
2024-02-26 | 561 RL 1 | Monitoring | HT Motor monitoring , Monitor carbon brush. Slip ring and starter condition
2024-02-26 | 54A WP 1 | Test local motor not run
2024-02-26 | 54A WP 2 | Uncouple motor found impeller full of rust | Uncouple motor found impeller full of rust. Clean impeller and fit back. Motor bearing ok. Test run ok.
2024-02-27 | 54A BM 1 | Starter problem | Check condition starter. Test manual ok. Lift up rheostart & check condition. Follow up needed.
2024-02-27 | 561 CP 1 | Compressor breakdown | Find cable for rental compressor 120mm3. Follow up needed.
2024-02-27 | 561 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-28 | 561 CP 2 | Cable not available | Lay temporary cable for rental compressor. 1 core 95 mm3 aluminium x 7 x 30 m connect at MCC and compressor. Follow up for testing.
2024-02-28 | 561 FN 2 | Troubleshoot | B05 1 01 - bearing temperature UAE. Replace transmitting. Test.
2024-02-28 | 552 RP 1 | maintenance routine | O&k Cement Mill 3 - Motor and starter maintenance
2024-02-28 | 552 RP 2 | maintenance routine | O&k Cement Mill 3 - Motor and starter maintenance
2024-02-28 | 545 FN 16 | maintenance routine | O&K CM3 - Motor and starter maintenance
2024-02-28 | 545 BM 1 | maintenance routine | O&K CM3 - Motor and starter maintenance
2024-02-28 | 590 VF 1 | Connect cable motor | Work together with normal group. Replace overload. Test.
2024-02-28 | 552 RP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-28 | 535 BC 5 | Not ready | Isolate & normalize supply
2024-02-29 | 561 CP 2 | Compressor testing | Rental compressor. Commissioning rental compressor. Unload - 150 A (R,Y,B). Load 230 A (R,Y,B)
2024-03-01 | 560 FN 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-01 | 561 CP 2 | Compressor installation | CNB 3:9:3.
2024-03-02 | 562 AD 1 | Alarm A23 | Isolate & normalize supply
2024-03-04 | 552 RP 1 | Monitoring | HT motor monitoring. Monitor carbon bruch, slip ring and starter condition for the following motor.
2024-03-04 | 552 RP 2 | Monitoring | HT motor monitoring. Monitor carbon bruch, slip ring and starter condition for the following motor.
2024-03-04 | 545 FN 16 | Monitoring | HT motor monitoring. Monitor carbon bruch, slip ring and starter condition for the following motor.
2024-03-04 | 545 BM 1 | Monitoring | HT motor monitoring. Monitor carbon bruch, slip ring and starter condition for the following motor.
2024-03-04 | 561 FN 2 | Monitoring | HT motor monitoring. Monitor carbon bruch, slip ring and starter condition for the following motor.
2024-03-04 | 561 RL 1 | Monitoring | HT motor monitoring. Monitor carbon bruch, slip ring and starter condition for the following motor.
2024-03-04 | 54A BM 1 | Troubleshoot | Starter. Connect back control cable and rotor cable. Check star point contactor. Ready for testing
2024-03-04 | 552 LC 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-04 | 552 LC 1 | Loose fuse | Tighten fuse
2024-03-04 | 555 VV 1 | Overload | Isolate & normalize supply
2024-03-04 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-04 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-04 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-04 | 552 RP 1 | Trip alarm machine fault | Check and found. 552 LQ1 temp fluctuate. Check found cable loose. Cut and rejoint cable. Test.
2024-03-04 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-04 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-04 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-05 | 545 BM 1 | Insulation test | Test for spare motor. Starter 6.6 kv - 0 ohm. 1000v - 15 m ohm
2024-03-05 | CM3 | Replace 1 pc LED sportlight. 100 watt | Replace 1 pc LED sportlight. 100 watt
2024-03-05 | 520 BC 1 | Overload | Isolate & normalize supply
2024-03-06 | 54A BM 1 | Test switchgear spring tension snap during test | Check and repeat another one testing. Send to PL1 reading for starter testing.
2024-03-06 | 54A HP 1 | service request: Oil supply pressure | check oil supply pressure.
2024-03-06 | 54A LP 1 | Low pressure no reading (short circuit) | Check and cable damage. Replace new cable.
2024-03-06 | 545 FM 1 | Return flow meter not showing reading at CCR | Isolate & normalize supply
2024-03-06 | 545 FN 4 | Alarm vibration 545 FN4 VD1. V41 | Reset failed. Follow up needed.
2024-03-07 | 545 FN 4 | Alarm vibration | Found bolt base sensor damaged. Tighten back. Reset at panel nearby motor. Start syatem.
2024-03-07 | 54A BM 1 | Motor Testing | Test control motor. Starter up and down position ok. Start point contactor ok. Switch gear open and close. Work complete for test.
2024-03-07 | 565 CP 3 | maintenance routine | Check at compressor alarm oil temperature and service. Follow up needed.
2024-03-08 | 545 BM 1 | Mill stop but GCB 13 still in close position | Manually open GCB at ER PPD. Bring back to workshop and service. Follow up needed.
2024-03-08 | 545 BM 1 | Mill cannot stop | Try manual stop. Bring GCB to workshop for check and repair. GCB cannot open and close. Mechanical problem. To find another GCB for check and repair. Replace 1 closing coil (733 ohm). Replace 1 tripping coil (43.6 ohm). Replace 2 stopper. Test open/close 3x. Rack in and handover to production. Need to repair 1 unit for spare.
2024-03-09 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-10 | 561 DL 1 | Check carbon brush and starter. trequest ny EE Azim. | All in good condition
2024-03-11 | 545 BM 1 | Switchgear | Try to repair and service but still cannot solve problem. Follow up needed.
2024-03-11 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-11 | 545 FM 1 | Flow meter not showing reading at CCR | Alarm at panel. Reset
2024-03-12 | 552 RP 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-12 | 552 RP 2 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-12 | 545 FN 16 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-12 | 545 BM 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-13 | 54A CP 1 | Pressure abnormal reading | Replace transmitter pressure but reading still show not normal. Follow up needed.
2024-03-14 | 545 TR 1 | Maintenance routine | Transformers inspection
2024-03-14 | 552 TR 1 | Maintenance routine | Transformers inspection
2024-03-14 | 54A TR 1 | Maintenance routine | Transformers inspection
2024-03-14 | 55B TR 1 | Maintenance routine | Transformers inspection
2024-03-14 | 561 TR 1 | Maintenance routine | Transformers inspection
2024-03-15 | 560 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-15 | 555 VV 1 | Both limit | Server limit switch. Test.
2024-03-15 | 561 FN 2 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-15 | 561 RL 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-15 | 562 CP 1 | maintenance routine | Greasing motor
2024-03-15 | 562 CP 2 | maintenance routine | Greasing motor
2024-03-15 | 562 CP 3 | maintenance routine | Greasing motor
2024-03-15 | 561 RL 1 | maintenance routine | Greasing motor
2024-03-15 | 561 FN 1 | maintenance routine | Greasing motor
2024-03-15 | 561 RL 1 | maintenance routine | Greasing motor
2024-03-15 | 561 FN 2 | maintenance routine | Greasing motor
2024-03-15 | 560 FN 1 | maintenance routine | Greasing motor
2024-03-16 | 561 RL 1 | Roller No.3. Alarm at panel (Burn out) | Isolate & normalize supply
2024-03-16 | 555 VV01 | Both limit on | Gate stuck. Service limit. Test.
2024-03-16 | 561 AL 01 | Service request: Isolate supply | Isolate & normalize supply
2024-03-18 | 561 FN 16 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 552 RP 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 552 RP 2 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 545 BM 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 561 FN 2 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 561 RL 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 545 FN 16 | pcs routine | Replace carbon brush 3 pcs
2024-03-18 | 561 RL 1 | Water level starter low | Topup water 12 liter
2024-03-18 | 545 BM 1 | Service GCB for 545 BM 1 but still not working | follow up needed
2024-03-18 | 552 CP 3 | Alarm starter feedback contact | Isolate & normalize supply
2024-03-18 | 510 AC 1 | Overload | Isolate & normalize supply
2024-03-18 | 561 FN 16 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 552 RP 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 552 RP 2 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 545 BM 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 561 FN 2 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 561 RL 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 555 VV 1 | Alarm runtime | Isolate & normalize supply
2024-03-20 | 542 BC 4 | Overload | Isolate & normalize supply
2024-03-20 | 552 BE 1 | Alarm high-high | Wire loose. Tighten wire.
2024-03-20 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-20 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-20 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 561 FN 2 | Water level starter low | Topup water 12 liter. Continue checking switchgear at workshop but still not ok. Follow up needed.
2024-03-21 | 561 RL 1 | Isolate supply | Rack out VCB
2024-03-21 | 561 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 540 WF 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 540 SX 2 | Overload (3x)y. 0.75 kw. 4 pole. | Reset, Clamp Amp R-1.8A, Y-0A, B-1.8A. Check found 1 phase coil open. replace motor. Test. clamp Amp. R-1.2A, Y-1.2A, B-1.2A.
2024-03-21 | 561 RL 1 | Service request: Isolate supply | Rack in VCB
2024-03-21 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-22 | 561 CLA1 | Check pump grease request by attendant | Check and setting timer.Test ok. Done work together with Mechanical team.
2024-03-22 | 545 SR 3 | Classifier inlet pressure reading fluctuate | Disconnect cable try. Continuty test. Found signal cable to AI no continuity suspect snap. Replace spare cable. (AI-22:6:6)
2024-03-23 | 535 BC 5 | Overload | Isolate & normalize supply
2024-03-23 | 555 CP 3 | Alarm overload at CCR | Check at CP alarm overload fan motor, Reset. Alarm service and alarm DP oil filter. Inform production and mechanical to continue check.
2024-03-24 | 555 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-24 | 542 MS 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-24 | 542 BC 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-24 | 555 CP 3 | Rental Comp -Cable incoming snap | Cut for 'vendor' to check compressor for futher action. Cable incoming has not been installed yet.
2024-03-24 | 552 BF 2 | Miller request to check not purging | Try local check supply. Check and troubleshoot found cable snap at card. Connector problem. Replace connector. Test local.
2024-03-24 | 542 BC 2 | Service request: Isolate supply | On MCCB
2024-03-24 | 542 MS 1 | Service request: run control | Loop terminal 1, 2, 3 for ready
2024-03-24 | 535 BC 5 | Not ready cover load | Isolate & normalize supply
2024-03-25 | 552 BE 1 | Alarm RP outlet chute level high | Service and clean level sensor. Done
2024-03-25 | 552 RP 1 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition
2024-03-25 | 552 RP 2 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition
2024-03-25 | 545 FN 16 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition
2024-03-25 | 545 BM 1 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition
2024-03-25 | 561 BM 1 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition
2024-03-25 | 561 FN 2 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition
2024-03-26 | 54A BM 1 | Troubleshoot | Replace socket 5 pin to 4 pin. lay cable for booster 30kw. Contactor service and cleaning 54 BM 1. Supervise contactor DC motor
2024-03-26 | 562 MW 1 | Overload | Isolate & normalize supply
2024-03-26 | 555 AL 1 LLPL41 (Hopper level) | Alarm level high | Check suspect sensor problem. Follow up needed.
2024-03-27 | 555 AL 1 | Continue from (Shift, Alarm hopper level high) | Replace level take form workshop.Test signal.
2024-03-27 | 562 MW 1 | Service request: Adjust gate | Adjust gate open. Close.
2024-03-27 | 552 CP 3 | Service request: Megger | Request megger motor
2024-03-27 | 542 MS 1 | Install panel. Connect cable supply and cable for DC. Waiting for cement mill stop for connect cable for site. Supervise contactor VC motor. | Install panel. Connect cable supply and cable for DC. Waiting for cement mill stop for connect cable for site. Supervise contactor VC motor.
2024-03-28 | 552 SG 3 | Alarm fault | Check found breaker. 48V trip. Reset.
2024-03-28 | 552 RF 1 | Service request: Alarm moveable roller left/high end | Check found 48V breaker trip. Try reset and start back still trip 48V breaker and same alarm hopper. Check sensor ok and gap at mimic 38 days and 40 days. Follow up needed.
2024-03-29 | 552 RP 1 | Troubleshoot | Reset start still trip. Continue check by normal group. Follow up needed.
2024-03-29 | 552 RP 1 | Troubleshoot | Check found 552 RP 2 TS 2 cable short (moveable roller temp no.high). Disconnect cable no: 57. Test.
2024-03-29 | 552 RP 1 | Troubleshoot | Continue check shift personal
2024-03-29 | 542 MS 1 | Troubleshoot | Connect cable & test.
2024-03-29 | 542 BC 2 | Troubleshoot | Connect cable & test.
2024-03-29 | 54A BM 1 | Monitoring | Supervise VC and hand over by VC Motor
2024-03-29 | 545 FM 2 | Alarm | Isolate & normalize supply
2024-03-30 | 552 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-30 | 562 MW 1 | Overload | Isolate & normalize supply
2024-03-30 | 562 MW 3 | Overload | Isolate & normalize supply
2024-03-30 | 562 MW 3 | Overload | Isolate & normalize supply
2024-03-31 | 562 MW 1 | Overload | Isolate & normalize supply
2024-03-31 | 562 MW 3 | Overload | Isolate & normalize supply
2024-03-31 | 561 CLA 1 | Overload | Check found cable snap. Repair &test.
2024-04-01 | 542 BF 2 | Not purging | Check no supply and card problem, have informed the normal group.
2024-04-01 | 552 RP 1 | Monitoring | HR Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-04-01 | 552 RP 2 | Monitoring | HR Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-04-01 | 545 FN 16 | Monitoring | HR Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-04-01 | 545 BM 9 | Monitoring | HR Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-04-01 | 561 RL 1 | Monitoring | HR Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-04-01 | 561 FN 2 | Monitoring | HR Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-04-01 | 561 RL 1 | Motor level starter show low | Topup water 12 liter at starter
2024-04-01 | 54A BM 1 | Insulation test | Test for Rotor-1kv - ohm. Stater- 5 kv-100m ohm. Cable- 5kv-800m ohm. Connect cable at GCB, compartment. Connect cable at terminat motor. On heater and add on extra heat rotor with spotlight.
2024-04-01 | 545 BF 2 | Troubleshoot | Check and rectify. Not purging. check and troubleshoot found card.
2024-04-01 | 542 BF 2 | Bag filter burnt | Bag filter, check and troubleshoot, found card burned 2 pcs.
2024-04-01 | 562 CP 3 | Main breaker trip. Megger motor shorted. | Dismantle motor.
2024-04-01 | 510 GA 3 | Overload | Isolate & normalize supply
2024-04-02 | 54A BM 1 | Insulation Test | Topup water for starter 84 liter. Add heater blower 2 pcs. Insulation test rotor. R-E - 1 KV -0.5 M Ohm. Y-E- 1 KV-0.5 M Ohm. B-E-1 KV - 0.5 M Ohm. Follow up needed.
2024-04-05 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-04-05 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-04-05 | 545 BM 1 | Trip MCCB | Cable nurn at terminal motor. Repair & test.
2024-04-06 | 545 BM 1 | Alarm not ready. * 18.5 kw, * 6 pole, * 35 A | Check MCCB Trip. Check found cable blue burn at terminal and touch yellow phase. Megger motor ok. Repair and replace terminal. Test ok. R-20.7A, Y-21.1A, B-20.7A.
2024-04-06 | 561 CLA 1 | Service request: run manual pump grease | By pass timer and select on local switch pump run. Pump on 2 hour and motor run 2 minute.
2024-04-06 | 561 CLA 1 | Service request: Isolate supply | Isolate & normalize supply
2024-04-06 | 545 FM 2 | Alarm stop machine | Reset panel
2024-04-06 | 561 CLA 1 | Motor on the gearbox | Disconnect cable motor
2024-04-07 | 561 CLA 1 | Service request: Isolate supply | Isolate & normalize supply
2024-04-07 | 561 CLA 1 | Vibration cable | Connect cable vibration
2024-04-08 | 54 A BM 1 | Insulation test | Test for starter & motor.
2024-04-09 | 545 BM 1 | Inching motor local switch problem | Check & service. Test.
2024-04-09 | 561 GR 1 | Overload | Isolate & normalize supply
2024-04-14 | 552 CP 3 | Assist shift | Rejoint cable & restart
2024-04-14 | 552 CP 3 | Alarm motor overload | Check found cable explode at terminal. Rejoint cable.
2024-04-15 | 561 CP 1 | Trip | Isolate & normalize supply
2024-04-15 | 545 FM 2 | Flow not show. Alarm AL60 AD fail | Isolate & normalize supply
2024-04-16 | 552 RP 1 | Starter fault | Starter not in position. Reset.
2024-04-16 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2024-04-16 | 561 BC 1 | Overload | Isolate & normalize supply
2024-04-16 | 545 FM 2 | Flow not show. | Isolate & normalize supply
2024-04-17 | 545 FM 2 | Flow not show | Isolate & normalize supply
2024-04-18 | 561 RL 1 | Monitoring | HT Motor monitoring, monitor carbon brush slip ring & starter condition
2024-04-18 | 561 FN 2 | Monitoring | HT Motor monitoring, monitor carbon brush slip ring & starter condition
2024-04-18 | 545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush slip ring & starter condition
2024-04-18 | 552 RP 1 | Monitoring | HT Motor monitoring, monitor carbon brush slip ring & starter condition
2024-04-18 | 552 RP 2 | Monitoring | HT Motor monitoring, monitor carbon brush slip ring & starter condition
2024-04-18 | 545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush slip ring & starter condition
2024-04-19 | 545 FM 2 | Alarm AL/60 AD fail | Isolate & normalize supply
2024-04-20 | 545 SF 1 | Door panel bag filter | Can't install lock door panel because not suitable with old lock
2024-04-22 | 561 FN 2 | Topup water 12 liter at starter | Topup water 12 liter at starter. Replace carbon brush 18 pcs. (E-carbon) direct change. Blow slip ring and filter.
2024-04-22 | 552 BC 2 | Service request: Isolate supply | Isolate & normalize supply
2024-04-22 | 540 BC 1 | Service request: Isolate supply | Isolate & normalize supply
2024-04-23 | 562 CP 3 | New Installation | Install motor CP at Cement Mill 4. Connect cable and test rotation, but wrong rotation. Change cable connection and test again.
2024-04-23 | Group 535 | Not ready. 48V trip | Terminal cable 23,24 short (D/S). Check D/S 535 BL 5. Service, repair, & test.
2024-04-23 | 542 FN 3 | Service request: Isolate supply | Isolate & normalize supply
2024-04-23 | 580 PG 2 | Cannot open/close | Rejoint cable and restart
2024-04-23 | 552 RP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-04-24 | 535 BC 2 | Service request: Isolate supply | Isolate & normalize supply
2024-04-24 | 535 BC 2 | Service request: Isolate supply | On MCCB
2024-04-24 | 545 FM 1 | Alarm AL/60 AD fail. Reading not showing at CCR. | Isolate & normalize supply
2024-04-24 | 545 FN 16 | Alarm not ready. Fan stop run | Check VCB. No alarm. Check starter no alarm. Ready to start. Restart inform to miller, monitor for one half an hour. If the condition is normal, continue start feed.
2024-04-25 | 54A BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-04-25 | 54A BE 2 | Service request: Isolate supply | Isolate & normalize supply
2024-04-25 | 54B SC 2 | Overload | Isolate & normalize supply
2024-04-25 | 54A BE 1 | Service request: Isolate supply | On MCCB
2024-04-25 | 54A BE 2 | Service request: Isolate supply | On MCCB

## C.Mill 3 (FYP)
Date | Equipment # | Issues | Resolution | Unnamed: 4 | Unnamed: 5 | Unnamed: 6 | equipment | count
2023-08-28 | 562 MW | Overload | Isolate & normalize supply
2023-09-14 | 552 RP 1 | Service request: Isolate supply | Rack out VCB
2023-09-14 | 553 RP 1 | Service request: Isolate supply | Rack out VCB
2023-09-15 | 552 RP 2
2023-09-16 | 553 RP 2
2023-08-25 | 51A GA S | Overload | Isolate & normalize supply
2023-08-25 | 520 BC 1 | Alarm return fault | Isolate & normalize supply
2023-08-25 | 520 GA 1 | Shaft snap | follow up needed
2023-08-25 | 520 SG 1 | Overload | Isolate & normalize supply
2023-08-28 | 535 BC 5 | Overload | Isolate & normalize supply
2023-09-07 | 535 BC 6 | Overload | Isolate & normalize supply
2023-09-07 | 535 BC 9 | Overload | Isolate & normalize supply
2023-08-29 | 535 BC 5 | Overload | Isolate & normalize supply
2023-09-05 | 540 SX 2 | Overload | Isolate & normalize supply
2023-09-14 | 545 FN 4 | Rack in ACB | Close ACB
2023-09-14 | 545 FN 4 | Rack out ACB | Open ACB
2023-09-08 | 54B AC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-09-08 | 54B AC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-09-08 | 54B AC 1 | Service request: Disconnect cable speed switch | Disconnect cable speed switch. Reset.
2023-08-31 | 550 FN 1 | Overload | Isolate & normalize supply
2023-09-02 | 552 BC 1 | Overload | Isolate & normalize supply
2023-08-28 | 552 BL 1 | Overload | Isolate & normalize supply
2023-09-11 | 552 BL 1 | Overload | Check coil motor at MCC. Restart.
2023-09-12 | 552 BL 1 | Overload | Isolate & normalize supply
2023-09-12 | 552 BL 1 | Overload | Isolate & normalize supply
2023-09-14 | 552 BL 1 | Overload | Isolate & normalize supply
2023-09-01 | 552 HT 1 | WO CE 786 - abnomal sound | Check and replace motor.
2023-08-25 | 552 RP 1 | Machine fault - starter not in high position | Isolate & normalize supply
2023-08-28 | 552 RP 1 | Alarm starter rods not in high position | Isolate & normalize supply
2023-09-14 | 552 RP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-09-14 | 552 RP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-08-25 | 552 SG 3 | Attendance info base portion | Replace new base an restart. Follow up needed.
2023-09-02 | 552 SG 3 | Overload | Isolate & normalize supply
2023-09-08 | 552 SG 3 | Overload | Isolate & normalize supply
2023-09-08 | 552 SG 3 | Overload | Isolate & normalize supply
2023-09-12 | 552 SG 3 | Overload | Isolate & normalize supply
2023-09-13 | 552 SG 3 | Overload | Isolate & normalize supply
2023-09-14 | 552 SG 3 | Overload | Isolate & normalize supply
2023-08-29 | 555 BF 3 | Overload | Isolate & normalize supply
2023-08-28 | 555 DY 1 | alarm cannot reset at panel (A09) | Isolate & normalize supply
2023-09-10 | 560 BC 1 | Overload | Isolate & normalize supply
2023-09-05 | 560 BF 3 | Overload | Isolate & normalize supply
2023-09-06 | 560 BF 3 | Overload | Isolate & normalize supply
2023-09-13 | 561 FN 2 | Maintenance routine | Top up 12 liter distill water for starter.
2023-09-06 | 561 PG 1 | Cannot moving - WO (EC791) | Replace valve
2023-09-09 | 561 RL 1 | Low pressure | Repair key way problem
2023-09-09 | 561 RL 1 | Alarm starter not in first step | Isolate & normalize supply
2023-09-14 | 561 RL 1 | Alarm starter not in first step | Isolate & normalize supply
2023-09-11 | 561 RL 4 | Alarm return fault at CCR | Tighten control cable at contector and aux contact
2023-09-01 | 561 RL 1 | WO CE 787 - Temp. fluctuate | Replace PT 101
2023-09-09 | 562 AD 1 | Alarm A25 | Isolate & normalize supply
2023-08-29 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-09-02 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-09-10 | 562 CP 1 | Fan motor overload | Isolate & normalize supply
2023-08-29 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-09-02 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-08-29 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-09-02 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-08-28 | 562 FN 1 | Overload | Isolate & normalize supply
2023-09-02 | 562 HT 1 | Service request | Service motor
2023-08-28 | 562 MW 3 | Overload | Isolate & normalize supply
2023-08-28 | 562 MW 1 | Gate not fully open at site. CCR open. | Adjust limit switch
2023-08-28 | CM3 | Trip | Isolate & normalize supply
2023-09-10 | CM3 | CM3 & CM4 running smoothly | Standby
2023-09-11 | CM3 : 1. 545 FN 14, 2. 545 FN 15, 3. 545 FN 16, 4. 545 SR 3, 5. 545 SR 1 , 6. 535 BC 4, 7. 552 BE 1, 8. 552 BE 2, 9. 542 BE 1, 10. 542 BE 2, 11. 550 FN 1, 12. 552 FN 2 | Maintenance routine | Greasing motor
2023-08-25 | Fire alarm | Alarm | Isolate & normalize supply
2023-09-13 | 1. 555 CP 3, 2. 552 CP 1 3. 552 CP 2, 4. 510 AC 1, 5. 545 FN 4, 6. 552 FN 1 | Maintenance routine | Greasing Motor
2023-09-13 | Gypsum weighfeeder | Calibration | Gypsum weighfeeder physical calibration done
2023-09-16 | 54B AC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-09-18 | 552 BC 2 | Service request: Isolate supply | Isolate & normalize supply
2023-09-18 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2023-09-18 | 552 BC 2 | Service request: Isolate supply | Isolate & normalize supply
2023-09-18 | 550 RF 2 | Overload | Isolate & normalize supply
2023-09-18 | T5481 | Material to cement silo temp - open loop | follow up needed
2023-09-20 | 545 BM 1 | C shift drive cannot start bush lifting fault | Alarm at Panel control motor for RR faulire. Try force camcon to up position but reached on step machinism stuck. check and found the steering lock not in position. Try manual stary from CCR.
2023-09-20 | 552 BL 1 | Overload | Isolate & normalize supply
2023-09-21 | 548 AC 1 | Check speed switch and ropeswitch | Check and replace speed switch and ropeswitch
2023-09-21 | T5481 | WO CE802 - open loop | Replace terminator
2023-09-22 | 560 BP 3 | Overload | Isolate & normalize supply
2023-09-22 | 5340 BP 2 | WO RE239 Overload- 0.75 kW | Check motor 1 phase missing - normal group continue replace motor space.
2023-09-25 | 545 FN 4 | Rack out ACB | Isolate & normalize supply
2023-09-25 | 560 BF 1 | Overload | Isolate & normalize supply
2023-09-25 | 510 BF 1 | Overload | Isolate & normalize supply
2023-09-25 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2023-09-25 | 561 BC 3 | Overload | Isolate & normalize supply
2023-09-25 | 51A GA S | Copper tank damage, gear for limit switch problem | Calibrate close/open gate
2023-09-26 | 560 BF 3 | Cable snap | Rejoint. Start but still trip overload. Disconnect cable and dismantle motor.
2023-09-26 | 552 BL 1 | Overload | Isolate & normalize supply
2023-09-27 | 560 BF 3 | New Installation | Prepare motor
2023-09-27 | 560 BF 3 | New Installation | Replace motor
2023-09-27 | 561 BC 3 | Overload | Isolate & normalize supply
2023-09-28 | 560 BP 3 | New Installation | test free run without load clamp amp. R= 11.64 Y=11.54 B=11.64
2023-09-28 | 560 BF 3 | Contactor stuck | Service contactor
2023-09-28 | Drayer CM3 | Trip overload breaker (alarm A09) | Service aux contact. Restart
2023-09-29 | CM3 - Stack 7 | Service request: Tidy up cable analog | Tidy up cable analog
2023-09-30 | 535 BC 5 | Overload | Isolate & normalize supply
2023-10-01 | CM3 | Running smoothly | Standby
2023-10-01 | 561 RL 1 | Alarm starter first stop | Isolate & normalize supply
2023-10-02 | 561 RL 1 | High vibration DE and NDE motor | Replace 22 pcs c/brush due to short. S/C 184291. WO-129160.
2023-10-02 | 561 BC 3 | Overload | Isolate & normalize supply
2023-10-02 | 560 RF 1 | Control breaker trip | Return fault
2023-10-02 | 561 BC 3 | cable snap | Rejoint cable and restart
2023-10-02 | 570 FN 1 | Overload | Isolate & normalize supply
2023-10-02 | 561 RL 1 | NDE/DE vibration alarm | Replace IFM sensor
2023-10-02 | 570 FN 1 | Motor short | Disconnect cable motor. Follow up needed.
2023-10-04 | 535 BC 2 | Service request: Isolate supply | off MCCB
2023-10-04 | 535 BC 5 | Service request: Isolate supply | off MCCB
2023-10-04 | 535 BC 2 | Service request: Isolate supply | on MSSB
2023-10-04 | 535 BC 5 | Service request: Isolate supply | on MSSB
2023-10-04 | 545 FN 16 | Service request: Isolate supply | Rack out VCB
2023-10-04 | 552 RP 1 | Service request: Isolate supply | Rack out VCB
2023-10-04 | 552 RP 1 | Service request: Isolate supply | Rack out VCB
2023-10-04 | 540 BC 1 | Service request: Isolate supply | off MCCB
2023-10-04 | 540 BC 2 | Service request: Isolate supply | off MCCB
2023-10-04 | 510 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-04 | 510 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-04 | 552 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-04 | 552 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-04 | 552 RP 1 | Maintenance routine | Check carbon/brush, s/ring and starter
2023-10-04 | 552 RP 1 | Maintenance routine | Check carbon/brush, s/ring and starter
2023-10-04 | 545 FN 16 | Maintenance routine | Check carbon/brush, s/ring and starter
2023-10-04 | 552 BL 2 | Check and test motor free run. | Test free run
2023-10-04 | 510 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-04 | 510 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 545 BM 1 | Service request: Isolate supply | Rack out GCR
2023-10-05 | 545 FN 4 | Service request: Normalize fuse form | Normalize fuse form
2023-10-05 | 545 SR 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 561 BC 3 | Overload | Isolate & normalize supply
2023-10-05 | 565 CP 3 | Service request: Isolate supply | Rack out ACB
2023-10-05 | 542 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 540 BC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 535 BC 4 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 552 RP 1 | Service request: Isolate supply | Rack in VCB
2023-10-05 | 552 RP 2 | Service request: Isolate supply | Rack in VCB
2023-10-05 | 545 BM 1 | Maintenance routine | Check brush lifting compartment and starter
2023-10-05 | 520 GA 1 | Service request: check gate | Adjust limit switch
2023-10-05 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 545 FN 16 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 552 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 552 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 535 BC 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 535 BC 5 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | CM3 | cable snap | Rejoint cable and restart
2023-10-05 | 540 BC 2 | alarm motion | Check and found base speed. Switch loose. Adjust & tighten bolt & nut. Restart.
2023-10-05 | 540 WF 1 | alarm CCP | Check & found emergency switch bad contact. Service & restart.
2023-10-05 | 545 FM 2 | AL10 alarm flow high | Isolate & normalize supply
2023-10-05 | 535 BC 4 | Service request: Isolate supply | Isolate & normalize supply
2023-10-05 | 540 BC 1 | alarm not ready | breakers supply off. Restart.
2023-10-05 | 54B AC 1 | Isolate supply req by Mech. | off MCCB - work done
2023-10-06 | 555 DY 1 | Alarm AO9 | Check found overload breaker trip. Reset.
2023-10-06 | 552 HT 1 | Alarm return fault at CCR | Check found aux contact running. (Return) damage replace. Restart.
2023-10-06 | 561 CP 1 | Trip by alarm element outlet temp. | Isolate & normalize supply
2023-10-07 | 552 SG 3 | Overload | Isolate & normalize supply
2023-10-09 | 561 TR 1 | Maintenance routine | Transformer inspection
2023-10-09 | 54A TR 1 | Maintenance routine | Transformer inspection
2023-10-09 | 54B TR 1 | Maintenance routine | Transformer inspection
2023-10-09 | 545 TR 1 | Maintenance routine | Transformer inspection
2023-10-09 | 552 TR 1 | Maintenance routine | Transformer inspection
2023-10-09 | 545 BM 1 | Operate motor | Isolate & normalize supply
2023-10-09 | 510 BF 2 | Overload | Isolate & normalize supply
2023-10-09 | 54B AC 1 | Not ready | Isolate & normalize supply
2023-10-09 | 510 BF 2 | Overload | Isolate & normalize supply
2023-10-09 | 54B AC 1 | Not ready | Isolate & normalize supply
2023-10-10 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 561 BC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 561 BC 4 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 54A BC 2 | Overload | Isolate & normalize supply
2023-10-10 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 561 BC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 561 BC 4 | Overload | Isolate & normalize supply
2023-10-10 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-10 | 562 CP 1 | Overload motor | Isolate & normalize supply
2023-10-10 | 562 CP 2 | Elemet outlet | Isolate & normalize supply
2023-10-11 | 55A BM 1 | Insulation test | Test for motor and starter at CM1 main drive
2023-10-11 | 510 BF 1 | Overload | Isolate & normalize supply
2023-10-11 | 545 FM 1 | Alarm | Isolate & normalize supply
2023-10-11 | 55A BM 1 | Maintenance routine | Blow dust and install heater
2023-10-12 | 561 PG 1 | WO CE 819 - Alarm run line | Service sensor. Tighten cable.
2023-10-12 | 552 SG 3 | Overload | Isolate & normalize supply
2023-10-13 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-13 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-13 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-10-13 | 561 WP 1 FY 1 FII (Flow control gate) | Control Valve (water) cement Mill 4 cannot control auto at CCR. | Replace positioner gate
2023-10-13 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-13 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-10-13 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-10-14 | 555 DY 1 | Contactor stuck | Replace contactor
2023-10-15 | CCR 2 | PC Cement Mill 3 blank | Rejoint loose cable
2023-10-15 | 552 RP 1 | Maintenance routine | HT Motor Monitoring
2023-10-15 | 552 RP 2 | Maintenance routine | HT Motor Monitoring
2023-10-15 | 545 FN 16 | Maintenance routine | HT Motor Monitoring
2023-10-15 | 546 BM 1 | Maintenance routine | HT Motor Monitoring
2023-10-15 | 561 FN 2 | Maintenance routine | HT Motor Monitoring
2023-10-15 | 561 RL 1 | Maintenance routine | HT Motor Monitoring
2023-10-15 | 561 CL 4 | Classifier lower bearing temp fluctuate | Tighten cable at terminat block. Start back still trip.(fluctuate) during start feed. Trace and suspect joint cable fault.(intermittent) cut and connect back at joint box. Restart.
2023-10-15 | 562 CP 2 | Alarm element outlet temp | Isolate & normalize supply
2023-10-16 | 55A BM 1 | Insulation Test | Stator 0 ohm. Direct short prepare new heater
2023-10-16 | 545 BM 1 | Insulation Test | Spare motor - Starter - 100 mn
2023-10-16 | 561 FN 4 | control breaker trip | Isolate & normalize supply
2023-10-16 | 550 DY 1 | Trip by alarm 409 (overload breaker) | Isolate & normalize supply
2023-10-16 | 550 DY 1 | Alarm A25 "high temp" time starting foam compressor activation not active in standby | Suspect contactor fault. Contactor 24V ac No spare. Check at w/shop found contactor 42V same model swapcoil test ok. Work done
2023-10-17 | 55A BM 1 | Insulation Test | Continue check still short add 1 heater.
2023-10-18 | 55A BM 1 | Insulation Test | Insulation test still short
2023-10-18 | 561 RL 1 | short | Replace 12 pcs c/brush
2023-10-19 | 555 CP 3 | Service request: Isolate supply | Open ACB
2023-10-19 | 55A BM 1 | Insulation Test | Motor stator - still short. Motor cable - 3.5 ohm
2023-10-19 | 540 WF 2 | Maintenance routine | Physical calibration
2023-10-21 | 562 AD 1 | Alarm A25 | Isolate & normalize supply
2023-10-21 | 561 BC 4 | Alarm motion detector | Check and found speed switch out of position. Adjust speed swirch and test ok. start back system.
2023-10-21 | 510 AC 1 | Overload | Isolate & normalize supply
2023-10-23 | 55A BM 1 | Insulation Test | Run motor.
2023-10-23 | 545 BM 1 | Insulation Test | Spare motor
2023-10-23 | 552 SG 3 | Overload | Isolate & normalize supply
2023-10-23 | 552 VV 1 | Breaker control trip | Isolate & normalize supply
2023-10-24 | 545 BM 1 | Service request: Tidy up cable | Spare motor clean water inside motor. Tidy up cable at CM3
2023-10-25 | 545 BM 1 | Service request: Tidy up cable | Tidy up cable
2023-10-26 | 561 RL 1 | Sparking | Check carbon brush
2023-10-26 | 561 BC 4 | WO CE 628 -Local switch not function | Replace local switch
2023-10-26 | 535 BC 5 | Overload | Isolate & normalize supply
2023-10-26 | 561 AL 1 | Rotor short to earth | Dismantle motor
2023-10-26 | 561 RL 105 | Troubleshoot | Disconnect cable & dismantle rotor inching.
2023-10-27 | 54 BC 2 | Overload | Isolate & normalize supply
2023-10-29 | 552 LQ2 TZ2 T02 | Temp. fluctuate | Check found cable loose at PT100. Tighten cable.
2023-10-29 | 561 CP 1 | Miller req to check alarm not ready | Isolate & normalize supply
2023-10-29 | 561 RL 105 | Motor Testing | Run motor.
2023-10-29 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2023-10-30 | 561 RL 1 | Motor Testing | Test motor main drive. Free run couple, 100 - 110 kw. 80 Amp / 79 Amp/ 81 Amp (Hyundai)
2023-11-02 | 550 RF 2 | Overload | Isolate & normalize supply
2023-11-04 | 561 GR 1 | Oil pressure low | Check found key master loose. Disconnect cable motor. Repair key motor.
2023-11-04 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2023-11-04 | 540 WF 2 | Alarm belt not feedback | Cannot reset. Req miller to call and check first. Try local. Alarm clear. Restart.
2023-11-05 | 561 GR 1 | Disconnect cable motor | Mech repair welding shaft motor p-up. Rejoint cable & test run.
2023-11-05 | 561 CP 1 | Alarm almost collect | Isolate & normalize supply
2023-11-05 | 562 CP 1 | Fan motor overload | Isolate & normalize supply
2023-11-05 | 561 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-11-05 | 561 GR 3 | Gear recover oil pressure low | Replace 1 pc solenoid valve (No.11). Solenoid valve Part No: DG4V-5-31B-M-PL-D-6-49
2023-11-05 | 562 GR 3 | gear recover oil pressure low | Replace 1 pc solenoid valve. Try start system & monitor, Work together with EE Haziruddin, EE Ikmal, Saifuddin. Solenoid valve part No: DG5V-H8-2A-P2-D-86-JA.
2023-11-05 | 563 GR 3 | Trip | Trip again with same alarm after mill running about 1 hour. * 561 GR01 TP5. *561 GR03M01 P43
2023-11-06 | 561 GR 1 | Troubleshoot | Check found welding crack dismantle motor to w/shop for modification. Modification by Machinist feedback and test ok.
2023-11-06 | 561 GR 3 | Troubleshoot | Gear reducer pump
2023-11-06 | 561 GR 1 | CM4 | Dismantle and install back motor. Modification motor & pump shaft.
2023-11-07 | 552 RP 1 | Maintenance routine (CNY 2024 stoppage) | Monitor for bearing replacing on CNY stopage. Motor c/brush, s/ring and starter for the following motor.
2023-11-07 | 552 RP 1 | Maintenance routine (CNY 2024 stoppage) | Monitor for bearing replacing on CNY stopage. Motor c/brush, s/ring and starter for the following motor.
2023-11-07 | 545 FN 16 | Maintenance routine (CNY 2024 stoppage) | Monitor for bearing replacing on CNY stopage. Motor c/brush, s/ring and starter for the following motor.
2023-11-07 | 545 BM 1 | Maintenance routine (CNY 2024 stoppage) | Monitor for bearing replacing on CNY stopage. Motor c/brush, s/ring and starter for the following motor.
2023-11-07 | 561 FN 2 | Maintenance routine (CNY 2024 stoppage) | Monitor for bearing replacing on CNY stopage. Motor c/brush, s/ring and starter for the following motor.
2023-11-07 | 561 RL 1 | Maintenance routine (CNY 2024 stoppage) | Monitor for bearing replacing on CNY stopage. Motor c/brush, s/ring and starter for the following motor.
2023-11-07 | 552 W 1 | Alarm key not auto | Check cable joint ok. Suspect local switch. Replace local switch ok. After a few minutes miller alarm, trace found cable snape. Cable no 1 and u joint back test ok.
2023-11-09 | 590 VF 1 | New Installation | Vibrating Feeder - Crusher China - Install spare motor and new base. WO CE 843.
2023-11-10 | 552 BI 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-10 | 552 BI 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-10 | 545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-11 | 543 BM 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-11 | 560 FN 1 | Overload | Isolate & normalize supply
2023-11-11 | 561 CP 2 | Alarm overload at CCR | Check at CP alarm service required. Check status alarm DP oil separator service max 0.80 bar. Reset
2023-11-12 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2023-11-12 | 545 FN 16 | Service request: Isolate supply | Isolate & normalize supply
2023-11-12 | 545 SR 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-12 | 545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-12 | 545 BM 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-12 | 562 CP 1 | Overload fan motor | Isolate & normalize supply
2023-11-12 | 562 CP 3 | Element outlet temp. high | Isolate & normalize supply
2023-11-13 | 552 RP 1 | Maintenance routine | Check c/brush - Blow motor, starter and carbon dust at s/ring compartment
2023-11-13 | 552 RP 2 | Maintenance routine | Check c/brush and s/ring condition. Blow motor, starter and carbon dust at s/ring compartment. Replace 2 pcs c.brush
2023-11-13 | 545 FN 16 | Maintenance routine | Check c/brush and s/ring condition. Blow motor, starter and carbon dust at s/ring compartment. Replace 5 pcs c.brush
2023-11-13 | 545 FN 16 | Service request: Isolate supply | Isolate & normalize supply
2023-11-13 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2023-11-14 | 545 SR 3 | Troubleshoot | Connect motor cable and tested
2023-11-14 | 561 RL 1 | Troubleshoot | Fit back cooling Fan ( Old motor)
2023-11-14 | 545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-14 | 545 SR 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-14 | 545 BM 1 | Alarm not ready | Rack in back
2023-11-14 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-17 | 552 PG 2 | WO :CE849 Alarm runtime after select to open | Check and found soleniod valve problem. Replace soleniod valve.
2023-11-18 | 552 PG 2 | WO :CE850 Alarm runtime after mech replace pneumatic Actuators valve | Check and found soleniod valve problem. Replace soleniod valve.
2023-11-18 | 550 FN 1 | Overload | Isolate & normalize supply
2023-11-19 | 555 AL 1 | WO CE851 Blow tank B not discharge | Replace pressure switch
2023-11-19 | 562 CD 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-19 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-11-19 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-19 | T5476 | Show open loop | Tighten cable t/c
2023-11-19 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-19 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-11-19 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-19 | 561 GR 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-20 | 561 BF 2 | Service request: Isolate supply | Isolate & normalize supply
2023-11-20 | 562 CP 1 | Element out let temp high 120 C | Isolate & normalize supply
2023-11-20 | 552 RP 1 | Monitoring | HT Motor Monitoring for the following motor
2023-11-20 | 552 RP 2 | Monitoring | HT Motor Monitoring for the following motor
2023-11-20 | 545 FN 14 | Monitoring | HT Motor Monitoring for the following motor
2023-11-20 | 545 BM 1 | Monitoring | HT Motor Monitoring for the following motor
2023-11-20 | 561 FN 2 | Monitoring | HT Motor Monitoring for the following motor
2023-11-20 | 561 RL 1 | Monitoring | HT Motor Monitoring for the following motor
2023-11-21 | 542 BE 1 | Isolate supply req by mech. | off MCCB
2023-11-21 | 561 RL 1 | Maintenance routine (CNY 2024 stoppage) | Monitor and survey motor for bearing replacement on CNY
2023-11-21 | 552 CP 2 | Trip | Isolate & normalize supply
2023-11-22 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-22 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-11-22 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-22 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-22 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-11-22 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-22 | 561 FN 2 | Short | Replace 8 pcs c/brush. Top up 12 liter distill water for starter. Top up 12 liter distill water for starter.
2023-11-22 | 561 RL 1 | Maintenance routine | Top up 24 liter distill water for starter
2023-11-22 | 561 DA 2 | cable snap | Rejoint cable and restart
2023-11-23 | 54A BM 1 | Insulation test | Inject 6kv - 0 ohm. Inject 1kv - 8 ohm
2023-11-23 | 545 BM 1 | Insulation test | Inject 6kv - 60 ohm. Inject 1kv - 100 ohm
2023-11-23 | 550 CP 1 | Control voltage fuse blow | replace control voltage fuse
2023-11-24 | 562 PP 1 | Valve not function | Replace and service valve
2023-11-24 | 562 CP 2 | Breaker F12 trip | Isolate & normalize supply
2023-11-24 | 552 RP 1 | Reset F12 trip | Isolate & normalize supply
2023-11-25 | 535 BC 6 | Overload | Isolate & normalize supply
2023-11-25 | 550 FN 1 | Overload | Isolate & normalize supply
2023-11-26 | 555 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-26 | 550 FN 1 | Overload coloum 24v error | Replace inverter
2023-11-26 | 550 FN 1 | Schneider panel problem | Change & install back card old panel & spare panel
2023-11-27 | 562 PP 1 | Service request: Check Blow tank A | Check valve. Check pipe. Suspect blockage
2023-11-27 | 555 AL 1 | Blow tank A not function | Check valve. Check found cable coil valve snap. Repair & test.
2023-11-28 | 540 SX 2 | Overload | Isolate & normalize supply
2023-11-28 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-11-28 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-11-28 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-11-29 | 552 VV 2 | Alarm run time | Check and found limit switch. Stuck. Service & test.
2023-11-29 | 545 FM 2 | AL 10 flow to high | Isolate & normalize supply
2023-11-30 | 561 RL 1 | Alarm mill liquid starter first step | Isolate & normalize supply
2023-11-30 | 561 RL 1 | Alarm state first step | Isolate & normalize supply
2023-12-02 | 535 BC 6 | Overload | Isolate & normalize supply
2023-12-02 | 552 CP 2 | Trip | Isolate & normalize supply
2023-12-03 | 552 RP 1 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
2023-12-03 | 552 RP 2 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
2023-12-03 | 545 FN 16 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
2023-12-03 | 545 BM 1 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
2023-12-03 | 561 RL 1 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
2023-12-03 | 561 FN 2 | Monitoring | HT Motor monitoring. Monitor c/brush, s/ring and starter for the following motor.
2023-12-03 | 540 SX 2 | Overload | Isolate & normalize supply
2023-12-03 | 540 BC 1 | Overload | Isolate & normalize supply
2023-12-03 | 540 BC 1 | Alarm motion detector | Check and found speed switch out of position. Calibrate
2023-12-04 | 555 BF 3 | Overload | Isolate & normalize supply
2023-12-04 | 545 FM 2 | AL10 flow too high | Isolate & normalize supply
2023-12-04 | 552 CP 2 | Overload | Isolate & normalize supply
2023-12-05 | 535 BC 4 | Maintenance routine | Greasing the following motor
2023-12-05 | 552 FN 1 | Maintenance routine | Greasing the following motor
2023-12-05 | 552 FN 2 | Maintenance routine | Greasing the following motor
2023-12-05 | 552 BE 1 | Maintenance routine | Greasing the following motor
2023-12-05 | 552 BE 2 | Maintenance routine | Greasing the following motor
2023-12-05 | 542 BE 1 | Maintenance routine | Greasing the following motor
2023-12-05 | 542 BE 2 | Maintenance routine | Greasing the following motor
2023-12-05 | 555 CP 3 | Maintenance routine | Greasing the following motor
2023-12-05 | 552 CP 1 | Maintenance routine | Greasing the following motor
2023-12-05 | 552 CP 2 | Maintenance routine | Greasing the following motor
2023-12-06 | 561 RL 1 | Service request: Isolate supply | Rack out GBC
2023-12-06 | 561 BC 3 | Overload | Isolate & normalize supply
2023-12-06 | 561 BC 3 | Cable speed switch snap (220V) | Rejoint cable and restart
2023-12-06 | 561 CR 2 | Alarm overload at CCR | Check at status DP air filter alarm reset
2023-12-06 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2023-12-06 | 560 BC 3 | Open coil | Check motor. Prepare for motor replacement.
2023-12-06 | 560 BC 3 | Install motor and install new motor | Test run local
2023-12-07 | 560 BC 3 | Service request: Isolate supply | Isolate & normalize supply
2023-12-08 | CM1 | Cable from PL1 to CM1 transformer | Check & megger cable.
2023-12-08 | 535 B 6 | Overload | Isolate & normalize supply
2023-12-11 | 552 LQ 3 | Not show flow at CCR | Check found coil socket snap and 1 cable snap. Replace new socket and cut joint back . Test run -ok
2023-12-11 | Stack 7 | Check at monitor alarm not response | Off and back supply to auto calibrate. Reading at 6.35
2023-12-12 | 561 FN 2 | Troubleshoot | To replaced 3 pcs c/brushes
2023-12-12 | 562 PP 1 | Troubleshoot | Change s/valve
2023-12-12 | 562 PP 2 | Troubleshoot | Change s/valve
2023-12-12 | 555 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 560 BC 1 | Troubleshoot | Load cell prebin
2023-12-12 | 561 BC 1 | Motor abnormal sound | Check test run
2023-12-12 | 555 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 545 FM 2 | AL10 flow too high | Isolate & normalize supply
2023-12-12 | 552 LC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 561 CP 2 | Alarm Dp air filter | Isolate & normalize supply
2023-12-12 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 560 BC 1 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 550 RF 2 | Overload | Isolate & normalize supply
2023-12-12 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-12-12 | 562 CP 1 | Overload from motor | Isolate & normalize supply
2023-12-13 | 552 RP 1 | Maintenance routine | Check carbon brush
2023-12-14 | 561 CP 2 | Breaker for cooling fan damage | Replace breaker
2023-12-14 | 561 CLA 1 | Local switch pole broken | Check found local switch pole broken. Repair.
2023-12-14 | 560 BE 1 | Alarm motion | Check found control breaker 220V Q148 trip reset.
2023-12-15 | 555 CP 3 | Alarm at temp | Isolate supply and normalize supply
2023-12-16 | 560 BF 3 | Overload | Isolate & normalize supply
2023-12-16 | 535 BC 5 | Overload | Isolate & normalize supply
2023-12-16 | 542 BC 4 | Overload | Isolate & normalize supply
2023-12-16 | 561 CP 1 | Overload | Isolate & normalize supply
2023-12-16 | 561 CP 2 | Can't start from CCR | Maintenance fault. Found CP in local mode. Change to remote.
2023-12-17 | 561 CP 2 | Overload fan motor | Isolate & normalize supply
2023-12-19 | 561 PG 1 | WO CE868 Alarm runtime | Check and found solenoid valve problem. Replace solenoid valve and test manual open & close.
2023-12-20 | 555 CP 3 | Service request: Isolate supply | Isolate supply and normalize supply
2023-12-21 | 552 CP 1 | Fault soft start | Isolate supply and normalize supply
2023-12-21 | Stacker Cement Mill | Cannot start | Check and found breaker 220V trip. MCCB 6. Trip cannot reset.Belt cannot reset. Suspect cable short. Follow up needed.
2023-12-22 | 510 GA 3 | Overload | Isolate & normalize supply
2023-12-22 | 510 BA 3 | Overload | Isolate & normalize supply
2023-12-23 | 555 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-12-23 | 545 FM 2 | AL10 flow to figh | Isolate & normalize supply
2023-12-24 | 535 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2023-12-25 | 552 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2023-12-25 | 552 BE 1 | Overload | Isolate & normalize supply
2023-12-26 | 545 BC 1 | Overload | Isolate & normalize supply
2023-12-26 | 545 RF 1 | Overload | Isolate & normalize supply
2024-12-28 | 561 RL 1 | Rack in GCB | Isolate & normalize supply
2024-12-28 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2024-12-31 | 535 BC 3 | Overload | Isolate & normalize supply
2024-12-31 | 535 BC 6 | Overload | Isolate & normalize supply
2024-01-01 | 552 RP 1 | Monitoring | HT Motor monitoring, motor c/brush, s/ring and starter condition.
2024-01-01 | 552 RP 2 | Monitoring | HT Motor monitoring, motor c/brush, s/ring and starter condition.
2024-01-01 | 545 FN 16 | Monitoring | HT Motor monitoring, motor c/brush, s/ring and starter condition.
2024-01-01 | 545 BM 1 | Monitoring | HT Motor monitoring, motor c/brush, s/ring and starter condition.
2024-01-01 | 561 FN 2 | Monitoring | HT Motor monitoring, motor c/brush, s/ring and starter condition.
2024-01-01 | 561 RL 1 | Monitoring | HT Motor monitoring, motor c/brush, s/ring and starter condition.
2024-01-03 | CM1 | Service request: Isolate supply | Rack in GCB
2024-01-03 | CM3 ER 7 | Trip incoming VCB | Close VCB
2024-01-03 | CM1 | Insulation test | Test for transformer. R-E: 700, Y-E: 700, B-E: 700
2024-01-03 | CM2 | cable punctured | Incoming Line 1 trip at MTS. Connect cable and normalize supply. Check and found cable CM1 transformer punctured behind CM2 w/feeder room.
2024-01-03 | CM3 | Insulation test | Test for transformer. R-E: 1.4 ohm, Y-E: 1.4 ohm, B-E: 1.4 ohm
2024-01-03 | CM4 | Insulation test | Test for cable main drive. R-E: 100 ohm, Y-E: 50 ohm, B-E: 25 ohm, R-Y: 14 ohm, R-B: 14 ohm, Y-B: 16 ohm
2024-01-03 | 545 FM 1 | AL10 flow to high | Isolate & normalize supply
2024-01-04 | 590 VF 1 | Motor Testing | To test motor. Motor rated 22A (hopper empty) R-38 A, Y-37.9 A, B-38 A
2024-01-04 | 590 VF 1 | Try release spring tension and test | R-30 A, Y-30.2 A, B-30.5 A
2024-01-04 | 590 VF 1 | Troubleshoot | Reposition motor and modified base motor test. R-21.5 A, Y-21.7 A, B-22 A
2024-01-04 | 590 VF 1 | Gearbox problem | R-23 A, Y-23 A, B-23 A. After few minute motor trip on 23 A O/L setting 24A. To be continue test due to 590 BC 1 gear box problem. Disconnect cable motor 590 BC 1
2024-01-05 | 542 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-01-05 | 54A FA 2 | Overload | Reset still not ok, Check and weight motor amp old ohm same. Check motor bearing stuck. Motor dismantle and already to workshop.
2024-01-06 | 54A FA 2 | New Installation | Install coupling at new motor. Install motor connect cable alignment. Test rotation and pleasure amp.
2024-01-06 | 54A FA 2 | Trip alarm A28 | Silo 1-1. Assist group shift to install motor
2024-01-08 | 562 AD 1 | Trip alarm A28 | Isolate & normalize supply
2024-01-08 | 561 FN 2 | short | Check c/brush. Top up 20 liter distill water for starter due to low level.
2024-01-08 | 561 RL 1 | maintenance routine | Check c/brush , s/ring and starter
2024-01-08 | 590 VF 1 | Test run | R-25.5, Y-25.5 , B-25.5
2024-01-08 | 590 VF 1 | After release spring | R-23.5, Y-23.5 , B-23.5
2024-01-08 | 590 VF 1 | motor overheat | Test free run 16A. Motor rated 22A.
2024-01-09 | 552 GA 1 | gate stuck | Isolate & normalize supply
2024-01-09 | 545 BM 1 | Insulation test | Test for spare motor. Starter R-E: 70 ohm, Y-E: 70 ohm, B-E: 70 ohm
2024-01-09 | 545 BM 1 | Insulation test | Test for spare motor. Starter R-E: 12 ohm, Y-E: 12 ohm, B-E: 12 ohm
2024-01-10 | 54A LP 1 | Insulation low and bearing jammed. | Service HEMT winding
2024-01-10 | 545 BM 1 | Motor Testing | Spare motor prepare space to relocate motor at warehouse.
2024-01-10 | 562 CP 1 | Overload fan motor | Isolate & normalize supply
2024-01-10 | 562 CP 1 | Isolate supply | Off MCCB
2024-01-10 | 562 CP 2 | Isolate supply | Off MCCB
2024-01-10 | 562 CP 3 | Isolate supply | Off MCCB
2024-01-11 | 510 AC 1 | Overload | Isolate & normalize supply
2024-01-11 | 510 AC 1 | Service request: Isolate supply | Isolate & normalize supply
2024-01-15 | CM1 | Transformer insulation test. | R: 900 ohm, Y: 900 ohm, B: 900 ohm
2024-01-15 | CM1 | Insulation test | Test for cable. R-E: 30 ohm, Y-E: 140 ohm, B-E: 100 ohm. Rejoint cable.
2024-01-15 | 54A LP 1 | New Installation | Reassemble motor. Replace 2 pcs bearing 6205 ZZ. Test run. R: 1.4 A, Y: 1.4 A, B: 1.5A. Motor 1.1 KW.
2024-01-15 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2024-01-15 | 562 CP 1 | Overload fan motor | Isolate & normalize supply
2024-01-17 | CM1 | Insulation test | Test for transformer. R-E: 1 ohm , Y-E: 1 ohm, B-E: 1 ohm
2024-01-17 | CM1 | cable punctured | 4 meter from join. Connect back supply from CM2 to CM1. Rack out incoming ACB CM1.
2024-01-17 | 545 BM 1 | Insulation test | Test for spare motor.
2024-01-17 | 535 BC 6 | Overload | Isolate & normalize supply
2024-01-18 | 552 RP 1 | maintenance routine | Check motor , carbon brush, s/ring and starter
2024-01-18 | 552 RP 2 | maintenance routine | Check motor , carbon brush, s/ring and starter
2024-01-19 | CM3 | WO: CE 879 : Miller request to check group. Group 545 and 535 trip. | Check at ER5 trip incoming. Check and found breaker for 545 FN 13 trip. Perform insulation test at terminal, result show motor short. Replace motor and test.
2024-01-19 | 545 FN 13 | Motor short | 15KW, 4 pole, 27.5 A. Taken record motor at workshop for replacement test run with fan. R-19-5 A, Y-19-5 A, B-19-4 A. Hand over to planner for alignment.
2024-01-19 | 550 FN 1 | New Installation | Install stopper and alignment panel inverter.
2024-01-21 | 552 BC 4 | Overload | Isolate & normalize supply
2024-01-22 | 552 RP 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-01-22 | 552 RP 2 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-01-22 | 545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-01-22 | 545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-01-22 | 561 FN 2 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-01-22 | 561 RL 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-01-22 | 542 BC 4 | Monitoring | Remonitoring LV Motor for bearing replacement on CNY.
2024-01-22 | 520 BC 8 | Monitoring | Remonitoring LV Motor for bearing replacement on CNY.
2024-01-22 | 550 BF 3 | Monitoring | Remonitoring LV Motor for bearing replacement on CNY.
2024-01-23 | 562 CP 1 | Isolate supply | Isolate & normalize supply
2024-01-23 | 562 CP 2 | Isolate supply | Isolate & normalize supply
2024-01-23 | 562 CP 3 | Isolate supply | Isolate & normalize supply
2024-01-23 | 561 CP 1 | Alarm | Isolate & normalize supply
2024-01-23 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-01-23 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-01-23 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-01-25 | 562 CP 1 | Overload from motor | Isolate & normalize supply
2024-01-28 | 562 AD 1 | Alarm A25 | Isolate & normalize supply
2024-01-29 | 55 B1 T1 | GCB always closing | Service
2024-01-29 | 545 BM 1 | Insulation test | Test for spare motor. Stator - R-E: 70 M ohm, Y-E: 70 M ohm, B-E: 70 M ohm
2024-01-29 | 545 BM 1 | Insulation test | Test for spare motor. Rotor - R-E: infiniti, Y-E: infiniti, B-E: infiniti
2024-01-29 | 55B 1T1 | GBC cannot tripping | Replace tripping coil for 55B 1T1 (CM2)
2024-01-29 | 562 CP 1 | Overload fan motor | Isolate & normalize supply
2024-01-29 | 561 CP 1 | Return fault at CCR | Check at Panel CP alarm starter feedback contact. Reset. Restart still return fault. Contactor not energize. Indicator " Comp run" at controller showing run. Attendant check oil leak. Try local motor still not run. Suspect safety sensor out off or controller problem. Need to follow up - trip.
2024-01-30 | 561 CP 2 | Not load | Disconnect, cut & rejoint cable.
2024-01-30 | 545 FN 4 | Isolate supply | Isolate & normalize supply
2024-01-30 | 545 FN 20 | Isolate supply | Isolate & normalize supply
2024-01-30 | 545 BM 1 | Isolate supply | Isolate & normalize supply
2024-01-30 | 561 BC 1 | Isolate supply | Isolate & normalize supply
2024-01-30 | 561 BC 4 | Isolate supply | Isolate & normalize supply
2024-01-30 | 552 FN 2 | Not ready | Isolate & normalize supply
2024-01-31 | 561 BC 4 | Overload | Isolate & normalize supply
2024-01-31 | 561 CP 2 | Socker valve problem | Repair socker valve
2024-01-31 | 562 AD 1 | Alarm 411, A09 | Isolate & normalize supply
2024-01-31 | 561 CP 1 | open switch | By pass temp switch
2024-01-31 | 54A BM 1 |  | Lay cable (fly) from MCC CM1, to main drive motor and to winding motor for heating. Motor already baricate. Amp - R-3.2A. Y-3.2A, B-3.2A.
2024-01-31 | 550 RF 2 | Overload | Isolate & normalize supply
2024-01-31 | 562 AD 1 | Dryer alarm A25 | Isolate & normalize supply
2024-02-01 | 552 RP 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-02-01 | 552 RP 2 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-02-01 | 545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-02-01 | 545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-02-01 | 561 FN 2 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-02-01 | 561 RL 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition.
2024-02-01 | 552 RP 1 | short | Replace 1 pc carbon brush
2024-02-01 | 562 AD 1 | Service request: Dryer check. Alarm A25 | Off & restart Dryer. Test ok
2024-02-01 | 552 CP 2 | Overload | Isolate & normalize supply
2024-02-02 | 54A BM 1 | Insulation test | Insert 6KV R-E- 0 M ohm, Y-E- 0 M ohm , B-e- 0 M ohm
2024-02-02 | 54A BM 1 | Insulation test | Insert 1 KV R-E- 15 M ohm, Y-E- 15 M ohm , B-E- 15 M ohm
2024-02-03 | 552 RP 1 | CE 885. Return fault | Check at panel VCB trip. Check motor found carbon crush sparking. Rack out VCB. Dismantlr carbon brush and holder. Megger : stator. Normal group continue skin slip ring-inprogress.
2024-02-03 | 552 RP 1 | Roller press motor CM3 | Checking motor.
2024-02-03 | 552 RP 1 | Roller press motor CM3 | Motor stationary site failure suspect carbon brush stuck holder cause sparking on slip ring.
2024-02-03 | 552 RP 1 | Monitoring | Visual inspection
2024-02-04 | 552 RP 1 | short | Check carbon brush and ring on stationary motor. Replace 1 pc carbon brush on movable motor
2024-02-04 | 552 RP 1 | short | Replace 1 pc carbon brush on movable motor
2024-02-05 | 552 RP 1 | Maintenance routine | Greasing motor
2024-02-05 | 552 RP 2 | Maintenance routine | Greasing motor
2024-02-05 | 561 FN 1 | Maintenance routine | Greasing motor
2024-02-05 | 561 FN 2 | Maintenance routine | Greasing motor
2024-02-05 | 561 RL 1 | Maintenance routine | Greasing motor
2024-02-05 | 561 CLA 1 | Maintenance routine | Greasing motor
2024-02-05 | 560 FN 1 | Maintenance routine | Greasing motor
2024-02-05 | 561 FN 3 | Maintenance routine | Greasing motor
2024-02-05 | 561 RL 1 | Maintenance routine | Greasing motor
2024-02-05 | 552 RP 1 | Maintenance routine | Check carbon brush & slip ring condition
2024-02-05 | 552 RP 2 | Maintenance routine | Check spring tension, carbon brush loosenes & starter condition
2024-02-06 | 561 TR 1 | Monitoring | Transformer inspection
2024-02-06 | 54A TR 1 | Monitoring | Transformer inspection
2024-02-06 | 54B TR 1 | Monitoring | Transformer inspection
2024-02-06 | 545 TR 1 | Maintenance routine | Transformer inspection
2024-02-06 | 552 TR 1 | Monitoring | Transformer inspection
2024-02-06 | 54A BM 1 | Troubleshoot | Disconnect cable supply for heating and bring to work shop
2024-02-06 | 535 BC 1 | Motor abnormal sound | Monitor bearing motor condition
2024-02-07 | 552 RP 1 | Maintenance routine (CNY 2024 stoppage) | Check carbon brush & slip ring contition ok. Check spring tension, carbon brush loosenes ok
2024-02-07 | 552 RP 2 | Maintenance routine (CNY 2024 stoppage) | Check carbon brush and slip ring contition ok. Check spring tension, carbon brush loosenes ok
2024-02-08 | 552 PP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-08 | 545 BM 1 | Isolate supply | Rack out GCB/VCB
2024-02-08 | 545 FN 16 | Isolate supply | Rack out GCB/VCB
2024-02-08 | 552 RP 1 | Isolate supply | Rack out GCB/VCB
2024-02-08 | 552 RP 2 | Isolate supply | Rack out GCB/VCB
2024-02-08 | 545 FN 14 | Isolate supply | Open ACB. Rack out.
2024-02-08 | 555 CP 3 | Isolate supply | Open ACB. Rack out.
2024-02-08 | 542 BE 1 | Isolate supply | Off MCCB
2024-02-08 | 552 BE 1 | Isolate supply | Off MCCB
2024-02-08 | 552 BE 2 | Isolate supply | Off MCCB
2024-02-08 | 540 BC 1 | Isolate supply | Off MCCB
2024-02-08 | 540 BC 2 M01 | Isolate supply | Off MCCB
2024-02-08 | 552 BE 1 M02 | Isolate supply | Off MCCB
2024-02-08 | 552 BE 2 M02 | Isolate supply | Off MCCB
2024-02-08 | 545 SR 1 | Isolate supply | Off MCCB
2024-02-08 | 545 SR 3 | Isolate supply | Off MCCB
2024-02-08 | 545 FN 15 | Isolate supply | Off MCCB
2024-02-08 | 545 SR 3 | Disconnect cable motor. | Work done
2024-02-08 | 545 FN 7 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 552 FN 7 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 545 FN 6 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 545 FN 8 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 550 BF 3 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 545 BF 2 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 542 BC 4 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 520 BC 8 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor CM3 & service
2024-02-08 | 545 FN 7 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 552 FN 7 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 545 FN 6 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 550 BF 3 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 545 BF 2 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 542 BC 4 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 520 BC 8 | Maintenance routine (CNY 2024 stoppage) | Motor LV maintenance - service motor
2024-02-08 | 552 LQ 1 | Maintenance routine (CNY 2024 stoppage) | Dismantle , service and install motor. Bearing No: LS: 6205ZZ, WO: EE 778
2024-02-08 | 552 LQ 1 | Maintenance routine (CNY 2024 stoppage) | Dismantle , service and install motor. Bearing No: OLS: 6204ZZ
2024-02-08 | 552 LQ 2 | Maintenance routine (CNY 2024 stoppage) | Dismantle , service and install motor. Bearing No: LS: 6305ZZ WO: EE 779
2024-02-08 | 552 LQ 2 | Maintenance routine (CNY 2024 stoppage) | Dismantle , service and install motor. Bearing No: OLS: 6204ZZ
2024-02-08 | 545 FN 1 | Maintenance routine (CNY 2024 stoppage) | Dismantle , service and install motor. Bearing No: LS: 6308ZZ WO: EE774
2024-02-08 | 545 FN 1 | Maintenance routine (CNY 2024 stoppage) | Dismantle , service and install motor. Bearing No: OLS: 6208ZZ
2024-02-08 | 545 FN 7 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6308
2024-02-08 | 545 FN 7 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6208
2024-02-08 | 552 FN 7 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6308
2024-02-08 | 552 FN 7 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6306
2024-02-08 | 545 FN 6 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6308
2024-02-08 | 545 FN 6 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6208
2024-02-08 | 545 FN 8 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6308
2024-02-08 | 545 FN 8 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6208
2024-02-08 | 550 BF 3 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6208
2024-02-08 | 550 BF 3 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6205
2024-02-08 | 545 BF 2 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6207
2024-02-08 | 545 BF 2 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6206
2024-02-08 | 542 BC 4 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6307
2024-02-08 | 542 BC 4 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6206
2024-02-08 | 520 BC 8 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6206
2024-02-08 | 520 BC 8 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6205
2024-02-08 | 545 FN 10 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6308
2024-02-08 | 545 FN 10 | Maintenance routine (CNY 2024 stoppage) | Bearing : 6208
2024-02-09 | 561 CP 2 | Alarm overload at CCR | Check at CP alarm. Service DP air filter
2024-02-09 | 542 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-09 | 542 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-09 | 562 AD 1 M01 | Alarm A25 | Isolate & normalize supply
2024-02-09 | Blow tank CM3 | Service request: Exhaust valve | Disconnect cable (220V)
2024-02-09 | 552 BE 2 M02 | Normalize fuse form | On MCCB
2024-02-09 | 552 CP 1 | Isolate supply | Off MCCB (Isolator)
2024-02-09 | 552 CP 2 | Isolate supply | Off MCCB (Isolator)
2024-02-09 | 540 WP 2 | Isolate supply | Off overload breaker
2024-02-09 | 542 BC 4 | Isolate supply | Off MCCB
2024-02-09 | 555 CP 3 | Isolate supply | Off MCCB
2024-02-09 | 535 BC 1 | Isolate supply | Off MCCB. Work done
2024-02-09 | 540 BC 1 | Normalize supply | On MCCB
2024-02-09 | 545 FN 7 | Maintenance routine (CNY 2024 stoppage) | Motor LV Maintenance - Service motor. Install motor at site. WO EE 765
2024-02-09 | 552 FN 7 | Motor LV Maintenance - Service motor. Install motor at site. WO EE 776 | Cement Mill & Packing CNY 2024 stoppage
2024-02-09 | 545 FN 6 | Maintenance routine (CNY 2024 stoppage) | Motor LV Maintenance - Service motor. Install motor at site. WO EE 766
2024-02-09 | 550 BF 3 | Motor LV Maintenance - Service motor. Install motor at site. WO EE 777 | Cement Mill & Packing CNY 2024 stoppage
2024-02-09 | 545 BF 2 | Maintenance routine (CNY 2024 stoppage) | Motor LV Maintenance - Service motor. Install motor at site. WO EE 769
2024-02-09 | 545 FN 13 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor and service .WO : EE 765
2024-02-09 | 545 FN 8 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor and service .WO : EE 767
2024-02-09 | 545 FN 10 | Maintenance routine (CNY 2024 stoppage) | Dismantle motor and service .WO : EE 773
2024-02-09 | 542 BC 4 | Maintenance routine (CNY 2024 stoppage) | ContInue service motor WO : EE 770/ oil seal
2024-02-09 | 520 BC 5 | Maintenance routine (CNY 2024 stoppage) | ContInue service motor WO : EE 772
2024-02-09 | 545 FN 7 | Installation | Install and dismantle motor CM3 - complete
2024-02-09 | 552 FN 7 | Installation | Install and dismantle motor CM3 - complete
2024-02-09 | 545 FN 6 | Installation | Install and dismantle motor CM3 - complete
2024-02-09 | 550 BF 3 | Installation | Install and dismantle motor CM3 - complete
2024-02-09 | 545 BF 2 | Installation | Install and dismantle motor CM3 - complete
2024-02-09 | 545 FN 10 | Installation | Install and dismantle motor CM3 - Ready to install. After completing the service do an insulation test
2024-02-09 | 520 BC 8 | Installation | Install and dismantle motor CM3 - Ready to install. After completing the service do an insulation test
2024-02-09 | 542 BC 4 | Installation | Install and dismantle motor CM3 - Ready to install. After completing the service do an insulation test
2024-02-09 | 545 FN 13 | Installation | Install and dismantle motor CM3 - Ready to install. After completing the service do an insulation test
2024-02-09 | 545 FN 8 | Installation | Install and dismantle motor CM3 - Ready to install. After completing the service do an insulation test
2024-02-10 | 552 BE M02 | Normalize supply | On MCCB
2024-02-10 | 552 BE M01 | Normalize fuse form | On MCCB
2024-02-10 | 552 BE M01 | Normalize fuse form | On MCCB
2024-02-10 | 535 VV 4 | New Installation (gate) | Install sensor close/open. Test signal open/close. Replace valve.Test local cannot operate. By pass piping still cannot open. Suspect gate stuck. Follow up needed. 19.7.2. Open. 19.7.3.Close. Command: 22.3.4
2024-02-10 | 545 FN 15 | Service request: Isolate supply | Isolate & normalize supply
2024-02-10 | 561 RL 1 M03 | Isolate supply | Off MCCB. Work done
2024-02-10 | 560 BC 1 | Isolate supply | Off MCCB. Work done
2024-02-10 | 561 BC 3 | Isolate supply | Off MCCB. Work done
2024-02-10 | 561 BC 4 | Isolate supply | Off MCCB. Work done
2024-02-10 | 545 FN 10 | Installation | Install motor CM3
2024-02-10 | 520 BC 8 | Installation | Install motor CM4
2024-02-10 | 542 BC 4 | Installation | Install motor CM5
2024-02-10 | 545 FN 8 | Installation | Install motor CM3
2024-02-10 | 545 FN 15 | Installation | Install motor CM3
2024-02-10 | 54A BM 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 55A TR 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 54B BM 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 55B TR 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 545 TR 1 | Maintenance routine | Cleaning TX room and TX
2024-02-10 | 552 TR 1 | Maintenance routine | Cleaning TX room and TX
2024-02-10 | 545 FN 16 | Installation | Install motor at site
2024-02-10 | 545 FN 8 | Installation | Install motor at site
2024-02-10 | 545 FN 10 | Installation | Install motor at site
2024-02-10 | 542 BC 4 | Installation | Install motor at site
2024-02-10 | 520 BC 8 | Installation | Install motor at site
2024-02-10 | 545 TR 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 552 TR 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 54A BM 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 560 TR 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 545 BM 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 54B TR 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 54B BM 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | 54B TR 1 | Power cut | Power cut Cement Mill & Packing plant
2024-02-10 | CM3 | Hoist not function | Check found supply. Genset not running. Genset problem 2x stop. Follow up needed.
2024-02-10 | 510 BE 1 | Isolate supply | Work done
2024-02-10 | 510 BE 2 | Isolate supply | Work done
2024-02-10 | 535 AC 1 | Isolate supply | Work done
2024-02-10 | 545 SR 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-10 | 545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-10 | 555 CP 3 | Normalize fuse form | On MCCB
2024-02-10 | 542 BE 2 | Normalize fuse form | On MCCB
2024-02-10 | 535 BC 1 | Normalize fuse form | On MCCB
2024-02-10 | 510 BE 2 | Normalize fuse form | On MCCB
2024-02-10 | 510 BE 1 | Normalize fuse form | On MCCB
2024-02-10 | 561 RL 1 | Service request: Isolate supply | VCB cannot work-out. Power cut off control breaker. Rack-out after power cut.
2024-02-10 | 545 SC 1 | Cover fan out position / motor no cooling fan | Install fan take from workshop and fix back cover fan.
2024-02-10 | 552 RP 1 | Check siren start warning | Check out put, relay output and supply 220V. Follow up needed.
2024-02-10 | 552 RP 2 | Check siren start warning | Check out put, relay output and supply 220V. Follow up needed.
2024-02-10 | 545 BM 1 | Check siren start warning | Check output, relay output and supply 220V. Follow up needed.
2024-02-11 | 545 FN 16 | Maintenance routine | WO: EE718. Motor and starter maintenance. Blow motor, slip ring and filter. IR test starter . R-E: 5 KV. Y-E: 5KV. B-E: 5KV. Lift up resistance starter and check all contact and resistor. Dismantle all fixed and moving contact bring back to workshop. Repair and service all the contact piece. Reinstall to starter, cleaning and renew oil.
2024-02-11 | 545 FN 16 | Maintenance routine | WO: EE718. Motor and starter maintenance. Blow motor, slip ring and filter. IR test rotor . R-E: 1 KV. Y-E: 1 KV. B-E: 1 KV. Lift up resistance starter and check all contact and resistor. Dismantle all fixed and moving contact bring back to workshop. Repair and service all the contact piece. Reinstall back to starter, cleaning and renew oil.
2024-02-11 | 545 FN 16 | Maintenance routine | Maintenance motor 545 FN 16 and starter. Insulation test starter 5 KV - 30 ohm - 3 minutes. Insulation test rotor 1 KV- Infinity 3 minutes. Replace oil starter 350 liter. Replace moving contact 6 pcs for start point and flatten the damaged all contact.
2024-02-11 | CM3 | Siren Mill. Siren roller press | Replace new siren. Siren roller press test.
2024-02-12 | 535 BC 9 | Normalize supply | On MCCB
2024-02-12 | 561 BC 4 | Normalize supply | On MCCB
2024-02-12 | 561 BC 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | 561 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | 560 BC 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | 561 BC 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | 561 RL 1 | Normalize fuse form | On MCCB
2024-02-12 | 561 BC 4 | Normalize fuse form | On MCCB
2024-02-12 | 560 BC 1 | Normalize fuse form | On MCCB
2024-02-12 | 561 BC 3 | Normalize fuse form | On MCCB
2024-02-12 | 545 FN 15 | Normalize fuse form | On MCCB
2024-02-12 | CM3 (Siren) | Not function | Check and troubleshoot. Supply okay. 220V. (Relay WN9 Siren). Relay WN 10 lamp. Replace new siren. Test. Siren: 13.6.1. Lamp:13.6.2.
2024-02-12 | 561 RL 1 | Normalize supply | On MCCB
2024-02-12 | CM3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | CM3 | Lay cable for main drive CM3 - damaged | Prepare for cable pointer. Follow up needed.
2024-02-12 | 535 BC 9 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | 561 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-12 | 535 AC 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 545 BE 1 | Isolate supply | Isolate & normalize supply
2024-02-13 | 540 BC 1 | Isolate supply | Isolate & normalize supply
2024-02-13 | 540 BC 2 | Isolate supply | Isolate & normalize supply
2024-02-13 | 542 BC 1 | Isolate supply | Isolate & normalize supply
2024-02-13 | 55B ITI Dept | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | CM3 (Exhaust valve blow tank) | A site: Cable snap | B site: Rejoint cable
2024-02-13 | 555 CP3 | Service request: Isolate supply | Rack in ACB
2024-02-13 | 510 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 510 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 542 BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 542 BE 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 562 AD 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 552 CP 3 | Not working | Check coil valve load unload
2024-02-13 | 545 BM1 | Cable punctured | Cut and reroute main drive cable. Training job have been carry on by cable jointer. Uncouple motor and test rotation. Amp per phase at power meter.
2024-02-13 | 545 FN 16 | Cable punctured | Cut and reroute cable. Jointing job have been carry on by cable jointer (Semmy). Cable size 16mm 3C XLPE
2024-02-13 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 545 SR 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 545 BM 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 542 BC 4 | Overload 4x | Isolate & normalize supply
2024-02-13 | 545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 561 RL 01 | Isolate supply | Isolate & normalize supply
2024-02-13 | 545 FN 4 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 545 SR 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 545 BM 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 542 BC 4 | Overload 4x | Isolate & normalize supply
2024-02-13 | 545 SR 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-13 | 561 RL 1 | Isolate supply | Isolate & normalize supply
2024-02-13 | 510 BC 1 | Motion | Adjust speed switch. Test.
2024-02-13 | 540 BC 2 | Motion | Adjust speed switch. Test.
2024-02-13 | 545 FN 15 | Motor Testing | Test rotation for motor
2024-02-13 | 545 FN 10 | Motor Testing | Test rotation for motor
2024-02-13 | 545 FN 16 | Motor Testing | Test run control for starter position
2024-02-13 | 545 BM 1 | Cable punctured | Uncouple motor and test rotation. Amp per phase of power meter. L1: 11A, L2: 1A, L3: 12A. Low per phase at power meter, L1:17KW, L2:10KW, L3:18KW.
2024-02-13 | 545 FN 16 | Cable punctured | Cut and reroute cable. Joining job have been calling on by cable jointer. Cable saiz 16mm 3C XCPE.
2024-02-13 | 545 FN 15 | Cable at terminal MCC burn | Cut & rejoint
2024-02-13 | 545 FN 16 | Insulation test | Insulation test cable, after jointer finish. Start local for test rotation
2024-02-14 | 552 RP 1 | HT Motor monitoring, monitor carbon brush, slip ring and starter condition | All motor are in good condition.
2024-02-14 | 552 RP 2 | HT Motor monitoring, monitor carbon brush, slip ring and starter condition | All motor are in good condition.
2024-02-14 | 545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-14 | 545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-14 | 552 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-14 | 555 DY 1 | Alarm A01 -HP. Alarm A09 - Compressor overload. | Blow panel. Service aux contact service pressure switch. Reset pressure switch. Alarm clear. Test.
2024-02-15 | 510 AC 1 | maintenance routine | Greasing motor
2024-02-15 | 552 RP 1 | maintenance routine | Greasing motor
2024-02-15 | 552 RP 2 | maintenance routine | Greasing motor
2024-02-15 | 545 FN 12 | maintenance routine | Greasing motor
2024-02-15 | 545 FN 4 | maintenance routine | Greasing motor
2024-02-15 | 552 PP 1 | maintenance routine | Greasing motor
2024-02-15 | 550 FN 1 | maintenance routine | Greasing motor
2024-02-15 | 545 FN 14 | maintenance routine | Greasing motor
2024-02-15 | 545 FN 16 | maintenance routine | Greasing motor
2024-02-15 | 545 SR 3 | maintenance routine | Greasing motor
2024-02-15 | 545 SR 1 | maintenance routine | Greasing motor
2024-02-15 | 535 BC 4 | maintenance routine | Greasing motor
2024-02-15 | 552 FN 1 | maintenance routine | Greasing motor
2024-02-15 | 552 FN 2 | maintenance routine | Greasing motor
2024-02-15 | 552 PG 2 | Service request: check gate open 30% only at CCR | Check at site gate open 60%. Found part looser. Tighten back. Test.
2024-02-15 | 535 BC 5 | Alarm not ready | Isolate & normalize supply
2024-02-16 | 562 CP 1 | Isolate supply | Done
2024-02-16 | 562 CP 2 | Isolate supply | Done
2024-02-16 | 562 CP 3 | Isolate supply | Done
2024-02-16 | 532 CP 3 | Isolate supply | Done
2024-02-16 | 5632 AD 1 | Trip breaker overload | Check found compressor problem. Coil unbalance RB 3.2 BY 19.2 RY 19.2 Ohm
2024-02-16 | 552 RP 1 | Calibration | Calibrate gap sensor
2024-02-16 | 552 RP 1 ZZ1Z01 | Calibration | Calibrate Gap sensor position left/Right
2024-02-16 | 552 RP 1 ZZ1Z02 | Calibration | Calibrate Gap sensor position left/Right
2024-02-16 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-16 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-16 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-16 | 545 FN 4 | Service request: Isolate supply | Rack ACB & close
2024-02-16 | 545 FN 1 | Reading not showing at CCR | Check alarm. AL60 AD fail. Reset.
2024-02-17 | 562 AD 1 Drayer Cement Mill 4 | Alarm A09 | Check and found overload breaker trip. Reset.
2024-02-18 | 562 AD 1 Drayer Cement Mill 4 | Trip alarm A09 | Reset overload breaker.
2024-02-19 | 552 RP 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-19 | 552 RP 2 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-19 | 545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-19 | 545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-19 | 561 FN 2 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-19 | 561 RL 1 | Monitoring | HT Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-02-19 | 545 FN 15 | Monitoring | Cleaning motor body for bearing replacement. Follow up needed.
2024-02-19 | 555 AL 1 | CM3 (Blow tank B cannot discharge) | Service and adjust breaket limit switch receiver (A). Test run.
2024-02-19 | 552 CP 1 | Safety interlock | Isolate & normalize supply
2024-02-19 | 545 BC 1 | Overload | Isolate & normalize supply
2024-02-19 | 552 RP 1 | Machine fault | Reset starter.
2024-02-20 | 552 LQ 3 | Service request: to check alarm level SW | Check grease at tank. Try start manual. No alarm. Check pressure switch & test. Found pressure switch & test.
2024-02-20 | 542 BC 4 | Overload | Isolate & normalize supply
2024-02-20 | 545 FN 15 | Winding motor full of grease | Cleaning
2024-02-20 | 552 LQ 3 | Alarm level low | Check found pressure switch problem. Taken record pressure switch at Mechanical workshop. Test.
2024-02-21 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-21 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-21 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-02-21 | 542 BE 1 | maintenance routine | Greasing the following motor
2024-02-21 | 542 BE 2 | maintenance routine | Greasing the following motor
2024-02-21 | 552 BE 1 | maintenance routine | Greasing the following motor
2024-02-21 | 552 BE 2 | maintenance routine | Greasing the following motor
2024-02-21 | 555 CP 3 | maintenance routine | Greasing the following motor
2024-02-21 | 552 CP 1 | maintenance routine | Greasing the following motor
2024-02-21 | 552 CP 2 | maintenance routine | Greasing the following motor
2024-02-21 | 562 CP 3 | maintenance routine | Greasing the following motor
2024-02-21 | 561 CP 1 | maintenance routine | Greasing the following motor
2024-02-21 | 561 CP 2 | maintenance routine | Greasing the following motor
2024-02-21 | 562 CP 1 | maintenance routine | Greasing the following motor
2024-02-21 | 562 CP 2 | maintenance routine | Greasing the following motor
2024-02-21 | 562 CP 3 | maintenance routine | Greasing the following motor
2024-02-21 | 561 FN 2 | maintenance routine | Monitor carbon brush and slip ring. Top up 12 liter distill water for starter
2024-02-21 | 561 RL 1 | maintenance routine | Monitor carbon brush and slip ring. Top up 12 liter distill water for starter
2024-02-21 | 562 AD 1 | Check alarm 23:Temp. Low | Isolate & normalize supply
2024-02-21 | 562 CP 1 | Service request: Isolate supply | ON MCCB
2024-02-21 | 562 CP 2 | Service request: Isolate supply | ON MCCB
2024-02-21 | 562 CP 3 | Service request: Isolate supply | ON MCCB
2024-02-21 | 562 AD 1 | Alarm A23. Temp Low | EE Azim request adjust by pass hot gas valve (VB).Temp showing. 0.7 C - 5 C. Still monitor. Inform to EE Azim.
2024-02-22 | 54A LP 1 | Motor Testing | Test motor at workshop after bearing replacement. R-1.6, Y-1.7, B-1.7 .Install at site. Need to test rotation
2024-02-23 | 535 BC 7 | Insulation test | R-150. Y-150 B-151
2024-02-23 | 54A AS 1 | Motor Testing | Test local run - condition ok.
2024-02-23 | 54A AS 2 | Motor Testing | Test local run - condition ok.
2024-02-23 | 54A DA 1 | Motor Testing | Test local run - condition ok.
2024-02-23 | 54A WP 2 | Insulation test | R-200. Y-200 B-201
2024-02-23 | 54A WF 1 | Insulation test | R-250. Y-250 B-250
2024-02-23 | 54A WF 2 | Insulation test | R-250. Y-250 B-250
2024-02-23 | 54A WF 3 | Insulation test | R-200. Y-200 B-201
2024-02-26 | 552 RP 1 | Monitoring | HT Motor monitoring , Monitor carbon brush. Slip ring and starter condition
2024-02-26 | 552 RP 2 | Monitoring | HT Motor monitoring , Monitor carbon brush. Slip ring and starter condition
2024-02-26 | 545 FN 16 | Monitoring | HT Motor monitoring , Monitor carbon brush. Slip ring and starter condition
2024-02-26 | 545 BM 1 | Monitoring | HT Motor monitoring , Monitor carbon brush. Slip ring and starter condition
2024-02-26 | 561 FN 2 | Monitoring | HT Motor monitoring , Monitor carbon brush. Slip ring and starter condition
2024-02-26 | 561 RL 1 | Monitoring | HT Motor monitoring , Monitor carbon brush. Slip ring and starter condition
2024-02-26 | 54A WP 1 | Test local motor not run
2024-02-26 | 54A WP 2 | Uncouple motor found impeller full of rust | Uncouple motor found impeller full of rust. Clean impeller and fit back. Motor bearing ok. Test run ok.
2024-02-27 | 54A BM 1 | Starter problem | Check condition starter. Test manual ok. Lift up rheostart & check condition. Follow up needed.
2024-02-27 | 561 CP 1 | Compressor breakdown | Find cable for rental compressor 120mm3. Follow up needed.
2024-02-27 | 561 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-02-28 | 561 CP 2 | Cable not available | Lay temporary cable for rental compressor. 1 core 95 mm3 aluminium x 7 x 30 m connect at MCC and compressor. Follow up for testing.
2024-02-28 | 561 FN 2 | Troubleshoot | B05 1 01 - bearing temperature UAE. Replace transmitting. Test.
2024-02-28 | 552 RP 1 | maintenance routine | O&k Cement Mill 3 - Motor and starter maintenance
2024-02-28 | 552 RP 2 | maintenance routine | O&k Cement Mill 3 - Motor and starter maintenance
2024-02-28 | 545 FN 16 | maintenance routine | O&K CM3 - Motor and starter maintenance
2024-02-28 | 545 BM 1 | maintenance routine | O&K CM3 - Motor and starter maintenance
2024-02-28 | 590 VF 1 | Connect cable motor | Work together with normal group. Replace overload. Test.
2024-02-28 | 552 RP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-02-28 | 535 BC 5 | Not ready | Isolate & normalize supply
2024-02-29 | 561 CP 2 | Compressor testing | Rental compressor. Commissioning rental compressor. Unload - 150 A (R,Y,B). Load 230 A (R,Y,B)
2024-03-01 | 560 FN 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-01 | 561 CP 2 | Compressor installation | CNB 3:9:3.
2024-03-02 | 562 AD 1 | Alarm A23 | Isolate & normalize supply
2024-03-04 | 552 RP 1 | Monitoring | HT motor monitoring. Monitor carbon bruch, slip ring and starter condition for the following motor.
2024-03-04 | 552 RP 2 | Monitoring | HT motor monitoring. Monitor carbon bruch, slip ring and starter condition for the following motor.
2024-03-04 | 545 FN 16 | Monitoring | HT motor monitoring. Monitor carbon bruch, slip ring and starter condition for the following motor.
2024-03-04 | 545 BM 1 | Monitoring | HT motor monitoring. Monitor carbon bruch, slip ring and starter condition for the following motor.
2024-03-04 | 561 FN 2 | Monitoring | HT motor monitoring. Monitor carbon bruch, slip ring and starter condition for the following motor.
2024-03-04 | 561 RL 1 | Monitoring | HT motor monitoring. Monitor carbon bruch, slip ring and starter condition for the following motor.
2024-03-04 | 54A BM 1 | Troubleshoot | Starter. Connect back control cable and rotor cable. Check star point contactor. Ready for testing
2024-03-04 | 552 LC 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-04 | 552 LC 1 | Loose fuse | Tighten fuse
2024-03-04 | 555 VV 1 | Overload | Isolate & normalize supply
2024-03-04 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-04 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-04 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-04 | 552 RP 1 | Trip alarm machine fault | Check and found. 552 LQ1 temp fluctuate. Check found cable loose. Cut and rejoint cable. Test.
2024-03-04 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-04 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-04 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-05 | 545 BM 1 | Insulation test | Test for spare motor. Starter 6.6 kv - 0 ohm. 1000v - 15 m ohm
2024-03-05 | CM3 | Replace 1 pc LED sportlight. 100 watt | Replace 1 pc LED sportlight. 100 watt
2024-03-05 | 520 BC 1 | Overload | Isolate & normalize supply
2024-03-06 | 54A BM 1 | Test switchgear spring tension snap during test | Check and repeat another one testing. Send to PL1 reading for starter testing.
2024-03-06 | 54A HP 1 | service request: Oil supply pressure | check oil supply pressure.
2024-03-06 | 54A LP 1 | Low pressure no reading (short circuit) | Check and cable damage. Replace new cable.
2024-03-06 | 545 FM 1 | Return flow meter not showing reading at CCR | Isolate & normalize supply
2024-03-06 | 545 FN 4 | Alarm vibration 545 FN4 VD1. V41 | Reset failed. Follow up needed.
2024-03-07 | 545 FN 4 | Alarm vibration | Found bolt base sensor damaged. Tighten back. Reset at panel nearby motor. Start syatem.
2024-03-07 | 54A BM 1 | Motor Testing | Test control motor. Starter up and down position ok. Start point contactor ok. Switch gear open and close. Work complete for test.
2024-03-07 | 565 CP 3 | maintenance routine | Check at compressor alarm oil temperature and service. Follow up needed.
2024-03-08 | 545 BM 1 | Mill stop but GCB 13 still in close position | Manually open GCB at ER PPD. Bring back to workshop and service. Follow up needed.
2024-03-08 | 545 BM 1 | Mill cannot stop | Try manual stop. Bring GCB to workshop for check and repair. GCB cannot open and close. Mechanical problem. To find another GCB for check and repair. Replace 1 closing coil (733 ohm). Replace 1 tripping coil (43.6 ohm). Replace 2 stopper. Test open/close 3x. Rack in and handover to production. Need to repair 1 unit for spare.
2024-03-09 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-09 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-10 | 561 DL 1 | Check carbon brush and starter. trequest ny EE Azim. | All in good condition
2024-03-11 | 545 BM 1 | Switchgear | Try to repair and service but still cannot solve problem. Follow up needed.
2024-03-11 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-11 | 545 FM 1 | Flow meter not showing reading at CCR | Alarm at panel. Reset
2024-03-12 | 552 RP 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-12 | 552 RP 2 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-12 | 545 FN 16 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-12 | 545 BM 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-13 | 54A CP 1 | Pressure abnormal reading | Replace transmitter pressure but reading still show not normal. Follow up needed.
2024-03-14 | 545 TR 1 | Maintenance routine | Transformers inspection
2024-03-14 | 552 TR 1 | Maintenance routine | Transformers inspection
2024-03-14 | 54A TR 1 | Maintenance routine | Transformers inspection
2024-03-14 | 55B TR 1 | Maintenance routine | Transformers inspection
2024-03-14 | 561 TR 1 | Maintenance routine | Transformers inspection
2024-03-15 | 560 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-15 | 555 VV 1 | Both limit | Server limit switch. Test.
2024-03-15 | 561 FN 2 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-15 | 561 RL 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-15 | 562 CP 1 | maintenance routine | Greasing motor
2024-03-15 | 562 CP 2 | maintenance routine | Greasing motor
2024-03-15 | 562 CP 3 | maintenance routine | Greasing motor
2024-03-15 | 561 RL 1 | maintenance routine | Greasing motor
2024-03-15 | 561 FN 1 | maintenance routine | Greasing motor
2024-03-15 | 561 RL 1 | maintenance routine | Greasing motor
2024-03-15 | 561 FN 2 | maintenance routine | Greasing motor
2024-03-15 | 560 FN 1 | maintenance routine | Greasing motor
2024-03-16 | 561 RL 1 | Roller No.3. Alarm at panel (Burn out) | Isolate & normalize supply
2024-03-16 | 555 VV01 | Both limit on | Gate stuck. Service limit. Test.
2024-03-16 | 561 AL 01 | Service request: Isolate supply | Isolate & normalize supply
2024-03-18 | 561 FN 16 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 552 RP 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 552 RP 2 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 545 BM 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 561 FN 2 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 561 RL 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 545 FN 16 | pcs routine | Replace carbon brush 3 pcs
2024-03-18 | 561 RL 1 | Water level starter low | Topup water 12 liter
2024-03-18 | 545 BM 1 | Service GCB for 545 BM 1 but still not working | follow up needed
2024-03-18 | 552 CP 3 | Alarm starter feedback contact | Isolate & normalize supply
2024-03-18 | 510 AC 1 | Overload | Isolate & normalize supply
2024-03-18 | 561 FN 16 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 552 RP 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 552 RP 2 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 545 BM 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 561 FN 2 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 561 RL 1 | Monitoring | HT motor monitoring, monitor carbon brush, slip ring and starter condition
2024-03-18 | 555 VV 1 | Alarm runtime | Isolate & normalize supply
2024-03-20 | 542 BC 4 | Overload | Isolate & normalize supply
2024-03-20 | 552 BE 1 | Alarm high-high | Wire loose. Tighten wire.
2024-03-20 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-20 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-20 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 561 FN 2 | Water level starter low | Topup water 12 liter. Continue checking switchgear at workshop but still not ok. Follow up needed.
2024-03-21 | 561 RL 1 | Isolate supply | Rack out VCB
2024-03-21 | 561 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 540 WF 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 540 SX 2 | Overload (3x)y. 0.75 kw. 4 pole. | Reset, Clamp Amp R-1.8A, Y-0A, B-1.8A. Check found 1 phase coil open. replace motor. Test. clamp Amp. R-1.2A, Y-1.2A, B-1.2A.
2024-03-21 | 561 RL 1 | Service request: Isolate supply | Rack in VCB
2024-03-21 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-21 | 562 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-22 | 561 CLA1 | Check pump grease request by attendant | Check and setting timer.Test ok. Done work together with Mechanical team.
2024-03-22 | 545 SR 3 | Classifier inlet pressure reading fluctuate | Disconnect cable try. Continuty test. Found signal cable to AI no continuity suspect snap. Replace spare cable. (AI-22:6:6)
2024-03-23 | 535 BC 5 | Overload | Isolate & normalize supply
2024-03-23 | 555 CP 3 | Alarm overload at CCR | Check at CP alarm overload fan motor, Reset. Alarm service and alarm DP oil filter. Inform production and mechanical to continue check.
2024-03-24 | 555 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-24 | 542 MS 1 | Service request: Isolate supply | Isolate & normalize supply
2024-03-24 | 542 BC 2 | Service request: Isolate supply | Isolate & normalize supply
2024-03-24 | 555 CP 3 | Rental Comp -Cable incoming snap | Cut for 'vendor' to check compressor for futher action. Cable incoming has not been installed yet.
2024-03-24 | 552 BF 2 | Miller request to check not purging | Try local check supply. Check and troubleshoot found cable snap at card. Connector problem. Replace connector. Test local.
2024-03-24 | 542 BC 2 | Service request: Isolate supply | On MCCB
2024-03-24 | 542 MS 1 | Service request: run control | Loop terminal 1, 2, 3 for ready
2024-03-24 | 535 BC 5 | Not ready cover load | Isolate & normalize supply
2024-03-25 | 552 BE 1 | Alarm RP outlet chute level high | Service and clean level sensor. Done
2024-03-25 | 552 RP 1 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition
2024-03-25 | 552 RP 2 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition
2024-03-25 | 545 FN 16 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition
2024-03-25 | 545 BM 1 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition
2024-03-25 | 561 BM 1 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition
2024-03-25 | 561 FN 2 | Monitoring | HT motor monitoring. Monitor carbon brush, slip ring and starter condition
2024-03-26 | 54A BM 1 | Troubleshoot | Replace socket 5 pin to 4 pin. lay cable for booster 30kw. Contactor service and cleaning 54 BM 1. Supervise contactor DC motor
2024-03-26 | 562 MW 1 | Overload | Isolate & normalize supply
2024-03-26 | 555 AL 1 LLPL41 (Hopper level) | Alarm level high | Check suspect sensor problem. Follow up needed.
2024-03-27 | 555 AL 1 | Continue from (Shift, Alarm hopper level high) | Replace level take form workshop.Test signal.
2024-03-27 | 562 MW 1 | Service request: Adjust gate | Adjust gate open. Close.
2024-03-27 | 552 CP 3 | Service request: Megger | Request megger motor
2024-03-27 | 542 MS 1 | Install panel. Connect cable supply and cable for DC. Waiting for cement mill stop for connect cable for site. Supervise contactor VC motor. | Install panel. Connect cable supply and cable for DC. Waiting for cement mill stop for connect cable for site. Supervise contactor VC motor.
2024-03-28 | 552 SG 3 | Alarm fault | Check found breaker. 48V trip. Reset.
2024-03-28 | 552 RF 1 | Service request: Alarm moveable roller left/high end | Check found 48V breaker trip. Try reset and start back still trip 48V breaker and same alarm hopper. Check sensor ok and gap at mimic 38 days and 40 days. Follow up needed.
2024-03-29 | 552 RP 1 | Troubleshoot | Reset start still trip. Continue check by normal group. Follow up needed.
2024-03-29 | 552 RP 1 | Troubleshoot | Check found 552 RP 2 TS 2 cable short (moveable roller temp no.high). Disconnect cable no: 57. Test.
2024-03-29 | 552 RP 1 | Troubleshoot | Continue check shift personal
2024-03-29 | 542 MS 1 | Troubleshoot | Connect cable & test.
2024-03-29 | 542 BC 2 | Troubleshoot | Connect cable & test.
2024-03-29 | 54A BM 1 | Monitoring | Supervise VC and hand over by VC Motor
2024-03-29 | 545 FM 2 | Alarm | Isolate & normalize supply
2024-03-30 | 552 CP 3 | Service request: Isolate supply | Isolate & normalize supply
2024-03-30 | 562 MW 1 | Overload | Isolate & normalize supply
2024-03-30 | 562 MW 3 | Overload | Isolate & normalize supply
2024-03-30 | 562 MW 3 | Overload | Isolate & normalize supply
2024-03-31 | 562 MW 1 | Overload | Isolate & normalize supply
2024-03-31 | 562 MW 3 | Overload | Isolate & normalize supply
2024-03-31 | 561 CLA 1 | Overload | Check found cable snap. Repair &test.
2024-04-01 | 542 BF 2 | Not purging | Check no supply and card problem, have informed the normal group.
2024-04-01 | 552 RP 1 | Monitoring | HR Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-04-01 | 552 RP 2 | Monitoring | HR Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-04-01 | 545 FN 16 | Monitoring | HR Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-04-01 | 545 BM 9 | Monitoring | HR Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-04-01 | 561 RL 1 | Monitoring | HR Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-04-01 | 561 FN 2 | Monitoring | HR Motor monitoring, monitor carbon brush, slip ring and starter condition
2024-04-01 | 561 RL 1 | Motor level starter show low | Topup water 12 liter at starter
2024-04-01 | 54A BM 1 | Insulation test | Test for Rotor-1kv - ohm. Stater- 5 kv-100m ohm. Cable- 5kv-800m ohm. Connect cable at GCB, compartment. Connect cable at terminat motor. On heater and add on extra heat rotor with spotlight.
2024-04-01 | 545 BF 2 | Troubleshoot | Check and rectify. Not purging. check and troubleshoot found card.
2024-04-01 | 542 BF 2 | Bag filter burnt | Bag filter, check and troubleshoot, found card burned 2 pcs.
2024-04-01 | 562 CP 3 | Main breaker trip. Megger motor shorted. | Dismantle motor.
2024-04-01 | 510 GA 3 | Overload | Isolate & normalize supply
2024-04-02 | 54A BM 1 | Insulation Test | Topup water for starter 84 liter. Add heater blower 2 pcs. Insulation test rotor. R-E - 1 KV -0.5 M Ohm. Y-E- 1 KV-0.5 M Ohm. B-E-1 KV - 0.5 M Ohm. Follow up needed.
2024-04-05 | 562 CP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-04-05 | 562 CP 2 | Service request: Isolate supply | Isolate & normalize supply
2024-04-05 | 545 BM 1 | Trip MCCB | Cable nurn at terminal motor. Repair & test.
2024-04-06 | 545 BM 1 | Alarm not ready. * 18.5 kw, * 6 pole, * 35 A | Check MCCB Trip. Check found cable blue burn at terminal and touch yellow phase. Megger motor ok. Repair and replace terminal. Test ok. R-20.7A, Y-21.1A, B-20.7A.
2024-04-06 | 561 CLA 1 | Service request: run manual pump grease | By pass timer and select on local switch pump run. Pump on 2 hour and motor run 2 minute.
2024-04-06 | 561 CLA 1 | Service request: Isolate supply | Isolate & normalize supply
2024-04-06 | 545 FM 2 | Alarm stop machine | Reset panel
2024-04-06 | 561 CLA 1 | Motor on the gearbox | Disconnect cable motor
2024-04-07 | 561 CLA 1 | Service request: Isolate supply | Isolate & normalize supply
2024-04-07 | 561 CLA 1 | Vibration cable | Connect cable vibration
2024-04-08 | 54 A BM 1 | Insulation test | Test for starter & motor.
2024-04-09 | 545 BM 1 | Inching motor local switch problem | Check & service. Test.
2024-04-09 | 561 GR 1 | Overload | Isolate & normalize supply
2024-04-14 | 552 CP 3 | Assist shift | Rejoint cable & restart
2024-04-14 | 552 CP 3 | Alarm motor overload | Check found cable explode at terminal. Rejoint cable.
2024-04-15 | 561 CP 1 | Trip | Isolate & normalize supply
2024-04-15 | 545 FM 2 | Flow not show. Alarm AL60 AD fail | Isolate & normalize supply
2024-04-16 | 552 RP 1 | Starter fault | Starter not in position. Reset.
2024-04-16 | 561 RL 1 | Service request: Isolate supply | Isolate & normalize supply
2024-04-16 | 561 BC 1 | Overload | Isolate & normalize supply
2024-04-16 | 545 FM 2 | Flow not show. | Isolate & normalize supply
2024-04-17 | 545 FM 2 | Flow not show | Isolate & normalize supply
2024-04-18 | 561 RL 1 | Monitoring | HT Motor monitoring, monitor carbon brush slip ring & starter condition
2024-04-18 | 561 FN 2 | Monitoring | HT Motor monitoring, monitor carbon brush slip ring & starter condition
2024-04-18 | 545 BM 1 | Monitoring | HT Motor monitoring, monitor carbon brush slip ring & starter condition
2024-04-18 | 552 RP 1 | Monitoring | HT Motor monitoring, monitor carbon brush slip ring & starter condition
2024-04-18 | 552 RP 2 | Monitoring | HT Motor monitoring, monitor carbon brush slip ring & starter condition
2024-04-18 | 545 FN 16 | Monitoring | HT Motor monitoring, monitor carbon brush slip ring & starter condition
2024-04-19 | 545 FM 2 | Alarm AL/60 AD fail | Isolate & normalize supply
2024-04-20 | 545 SF 1 | Door panel bag filter | Can't install lock door panel because not suitable with old lock
2024-04-22 | 561 FN 2 | Topup water 12 liter at starter | Topup water 12 liter at starter. Replace carbon brush 18 pcs. (E-carbon) direct change. Blow slip ring and filter.
2024-04-22 | 552 BC 2 | Service request: Isolate supply | Isolate & normalize supply
2024-04-22 | 540 BC 1 | Service request: Isolate supply | Isolate & normalize supply
2024-04-23 | 562 CP 3 | New Installation | Install motor CP at Cement Mill 4. Connect cable and test rotation, but wrong rotation. Change cable connection and test again.
2024-04-23 | Group 535 | Not ready. 48V trip | Terminal cable 23,24 short (D/S). Check D/S 535 BL 5. Service, repair, & test.
2024-04-23 | 542 FN 3 | Service request: Isolate supply | Isolate & normalize supply
2024-04-23 | 580 PG 2 | Cannot open/close | Rejoint cable and restart
2024-04-23 | 552 RP 1 | Service request: Isolate supply | Isolate & normalize supply
2024-04-24 | 535 BC 2 | Service request: Isolate supply | Isolate & normalize supply
2024-04-24 | 535 BC 2 | Service request: Isolate supply | On MCCB
2024-04-24 | 545 FM 1 | Alarm AL/60 AD fail. Reading not showing at CCR. | Isolate & normalize supply
2024-04-24 | 545 FN 16 | Alarm not ready. Fan stop run | Check VCB. No alarm. Check starter no alarm. Ready to start. Restart inform to miller, monitor for one half an hour. If the condition is normal, continue start feed.
2024-04-25 | 54A BE 1 | Service request: Isolate supply | Isolate & normalize supply
2024-04-25 | 54A BE 2 | Service request: Isolate supply | Isolate & normalize supply
2024-04-25 | 54B SC 2 | Overload | Isolate & normalize supply
2024-04-25 | 54A BE 1 | Service request: Isolate supply | On MCCB
2024-04-25 | 54A BE 2 | Service request: Isolate supply | On MCCB
2024-12-31 | 535 BC 5 | motor overheat | Restart machine after 15 minutes